Application No.:  391009

Equipment Category – I.C. Engine, Landfill Gas-Fired

| 1. GENERAL INFORMATION |  | DATE: 2/20/2003 |
| --- | --- | --- |
| a. manufacturer: Deutz |
| b. type: | c. model: TBG620V16K |
| d. style: |
| e. applicable aqmd rules: 1110.2, 1150.1, 431.1 |
| f. cost: $ () source of cost data: |
| g. operating schedule: 24 hrs/day 7 days/wk 52 wks/yr |

| 2. EQUIPMENT INFORMATION |  | App. No.: 391009 |
| --- | --- | --- |
| A. FUNCTION: Power Generation |
| B. maximum Heat Input: 14.7 MMBtu/hr | C. maximum throughput: 1850 bhp |
| D. burner information: no.: type: |
| e. primary fuel: Landfill Gas | f. other fuel: None |
| g. operating conditions: Expected to be steady, at or near full capacity. |

| 3. COMPANY INFORMATION |  | App. No.: 391009 |
| --- | --- | --- |
| A. NAME: MM San Bernardino Energy, LLC | B. SIC CODE: 4953 |
| C. ADDRESS: Milliken Landfill, 2050 S. Milliken Ave. CITY: Ontario STATE: CA ZIP: 91761 |
| D. CONTACT PERSON: Ben Huiser | E. PHONE NO.: 612-373-5464 |

| 4. PERMIT INFORMATION |  | App. No.: 391009 |
| --- | --- | --- |
| A. AGENCY: SCAQMD | B. application type: |
| C. AGENCY CONTACT PERSON: Ted Kowalczyk | D. PHONE NO.: 909-396-2592 |
| E. PERMIT TO CONSTRUCT/OPERATE INFORMATION: P/C NO.: 391009 ISSUANCE DATE: 5/16/2002 check if no p/c P/O NO.: ISSUANCE DATE: |
| F. START-UP DATE: |

| 5. EMISSION INFORMATION |  | App. No.: 391009 |
| --- | --- | --- |
| A. PERMIT |
| A1. PERMIT LIMIT: Lb/hr (g/bhp-hr): ROG-3.27 (0.8), NO2-2.44 (0.6), CO-10.2 (2.5), SO2-0.10, PM-0.20. Engine must be equipped with air/fuel ratio controller, and flue gas O2 must be checked weekly. Heat input to the engine not to exceed 14.7 MMBtu/hr. |
| A2. bact/lAer DETERMINATION: g/bhp-hr: NOx- 0.6, VOC- 0.8, CO- 2.5. |
| a3. BASIS OF THE BACT/LAER DETERMINATION: SCAQMD BACT Guidelines, Part D. |
| B. CONTROL TECHNOLOGY |
| B1. MANUFACTURER/SUPPLIER: Duetz |
| B2. TYPE: Engine Design |
| B3. DESCRIPTION: Engine is turbocharged and intercooled and has an air/fuel ratio controller. |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: ISSUANCE DATE: P/O NO.: ISSUANCE DATE: |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: |
| B6. WARRANTY: PPMVD@15%O2: NOx-46, CO-360, HC-79. g/hp-hr: ROG <.02, PM-10 <.05 (Based on 34% (HHV) engine efficiency used by the manufacture in his calculations, the PPMVD limits correspond to the following g/hp-hr: NOx-0.61, CO-2.9, HC-0.36 (as methane). |
| B7. PRIMARY POLLUTANTS: NOx, CO, VOC, PM, SOx |
| B8. SECONDARY POLLUTANTS: |
| B9. SPACE REQUIREMENT: |
| B10. LIMITATIONS: | B11. UNUSED |
| B12. OPERATING HISTORY: |
| B13. UNUSED | B14. UNUSED |
| C. CONTROL EQUIPMENT COSTS |
| C1. CAPITAL COST: check if installation cost is included in EQUIPMENT cost EQUIPMENT: $ INSTALLATION: $ () SOURCE OF COST DATA: |
| C2. ANNUAL OPERATING COST: $ () SOURCE OF COST DATA: |
| D. DEMONSTRATION OF COMPLIANCE |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: DATE: |
| D2. COMPLIANCE DEMONSTRATION: |
| D3. VARIANCE: NO. OF VARIANCES: DATES: CAUSES: |
| D4. VIOLATION: NO. OF VIOLATIONS: DATES: CAUSES: |
| D5. MAINTENANCE REQUIREMENTS: | D6. UNUSED |
| D7. SOURCE TEST/PERFORMANCE DATA RESULTS AND ANALYSIS: DATE OF SOURCE TEST: Source test is required within 120 days following startup. CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICIENCY: SOURCE TEST/PERFORMANCE DATA: OPERATING CONDITIONS: TEST METHODS: |

| 6. COMMENTS |  | App. No.: 391009 |
| --- | --- | --- |