Application No.:  388050

Equipment Category – I.C. Engine, Digester Gas-Fired

| 1. GENERAL INFORMATION |  | DATE: 7/18/2002 |
| --- | --- | --- |
| a. manufacturer: Waukesha |
| b. type: Spark Ignition, 4-Cycle | c. model: L7042GL |
| d. style: |
| e. applicable aqmd rules: 431.1, 1110.2 |
| f. cost: $ () source of cost data: |
| g. operating schedule: 24 hrs/day 7 days/wk 52 wks/yr |

| 2. EQUIPMENT INFORMATION |  | App. No.: 388050 |
| --- | --- | --- |
| A. FUNCTION: Power Generation |
| B. maximum Heat Input: 10.75 MMBtu/hr | C. maximum throughput: 1408 bhp |
| D. burner information: no.: type: |
| e. primary fuel: Digester Gas (dairy manure biogas) | f. other fuel: natural gas/air blend |
| g. operating conditions: Expected to be steady, at or near full capacity |

| 3. COMPANY INFORMATION |  | App. No.: 388050 |
| --- | --- | --- |
| A. NAME: Chino Basin Desalter Authority ( initial applicant was Inland Empire Utilities Agency) | B. SIC CODE: 4941 |
| C. ADDRESS: 6905 Kimball Ave. CITY: Chino STATE: CA ZIP: 91710 |
| D. CONTACT PERSON: Julio Im | E. PHONE NO.: 909-993-1649 |

| 4. PERMIT INFORMATION |  | App. No.: 388050 |
| --- | --- | --- |
| A. AGENCY: SCAQMD | B. application type: |
| C. AGENCY CONTACT PERSON: Guarang Rawal | D. PHONE NO.: 909-396-2543 |
| E. PERMIT TO CONSTRUCT/OPERATE INFORMATION: P/C NO.: 388050 ISSUANCE DATE: 6/18/2002 check if no p/c P/O NO.: ISSUANCE DATE: |
| F. START-UP DATE: Startup testing in progress |

| 5. EMISSION INFORMATION |  | App. No.: 388050 |
| --- | --- | --- |
| A. PERMIT |
| A1. PERMIT LIMIT: PPMVD@15%O2 (lb/hr): NOx-47 (1.86), CO-2000 (7.75), ROG-325 (2.48). lb/hr: PM10-0.20, SOx-0.12. Compliance with Rule 431.1 (sulfur content of fuel not to exceed 40 ppmv as H2S). Heat input to the engine not to exceed 10.75 MMBtu/hr based on hourly average. |
| A2. bact/lAer DETERMINATION: g/bhp-hr: NOx- 0.6, VOC- 0.8, CO- 2.5. Compliance with Rule 431.1. |
| a3. BASIS OF THE BACT/LAER DETERMINATION: SCAQMD BACT Guidelines, Part D. |
| B. CONTROL TECHNOLOGY |
| B1. MANUFACTURER/SUPPLIER: Waukesha |
| B2. TYPE: Engine design |
| B3. DESCRIPTION: Engine is turbocharged, intercooled and lean-burn with an air/fuel ratio controller. |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: ISSUANCE DATE: P/O NO.: ISSUANCE DATE: |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: |
| B6. WARRANTY: Engine is guaranteed to meet AQMD BACT emission limits |
| B7. PRIMARY POLLUTANTS: NOx, CO, VOC, PM, SOx |
| B8. SECONDARY POLLUTANTS: |
| B9. SPACE REQUIREMENT: |
| B10. LIMITATIONS: | B11. UNUSED |
| B12. OPERATING HISTORY: |
| B13. UNUSED | B14. UNUSED |
| C. CONTROL EQUIPMENT COSTS |
| C1. CAPITAL COST: check if installation cost is included in EQUIPMENT cost EQUIPMENT: $ INSTALLATION: $ () SOURCE OF COST DATA: |
| C2. ANNUAL OPERATING COST: $ () SOURCE OF COST DATA: |
| D. DEMONSTRATION OF COMPLIANCE |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: DATE: |
| D2. COMPLIANCE DEMONSTRATION: |
| D3. VARIANCE: NO. OF VARIANCES: DATES: CAUSES: |
| D4. VIOLATION: NO. OF VIOLATIONS: DATES: CAUSES: |
| D5. MAINTENANCE REQUIREMENTS: | D6. UNUSED |
| D7. SOURCE TEST/PERFORMANCE DATA RESULTS AND ANALYSIS: DATE OF SOURCE TEST: Source test is required within 180 days following startup. CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICIENCY: SOURCE TEST/PERFORMANCE DATA: OPERATING CONDITIONS: TEST METHODS: |

| 6. COMMENTS |  | App. No.: 388050 |
| --- | --- | --- |
| The concentration limits in Section A1 are based on compliance with Rule 1110.2, not BACT. However, the pound-per-hour limits are based on the BACT emission factors in Section A2. Concentration or emission factor limits based on BACT will be placed in the permit when the Permit to Operate is issued. After issuance of the Permit to Construct, ownership of the facility changed from Inland Empire Utilities Agency to Chino Basin Desalter Authority. To refelect this change, the original application, 388050, was cancelled and replaced by 411148. |