## Average Boiler Size
Proposed Regulation to Implement the California Cap-and-Trade Program: Supplemental Materials for the Compliance Pathways Analysis (Staff Report Chapter V and Appendix F)
Available for download at http://www.arb.ca.gov/regact/2010/capandtrade10/capandtrade10.htm
2010-10-29
Further references for this spreadsheet (i.e., beyond what is listed below) can be found in the Cap-and-Trade Regulation Staff Report References and/or Appendix F.
Sub-Sector | Percent of Fuel Use By Steam | Assumptions |  |  |  | Calculations
|  | Boiler Size Category (MMBTU/hr) | Unit Size (MMTBTU/hr) | Efficiency (percent) | Capacity Factor (staff estimate) (percent) | Number of Total Boilers | Fuel Use Per Unit (MMBTU) | 2008 Emissions (MTCO2e) | Amount of Natural Gas to Produce Steam (MMBTU)
Petroleum | 33.71% | >60 | 100 | 80-83 | 0.9 | 282.3993 | 788400 | 35006223.7928 | 222643607.529
Food | 63.92% | 10-100 | 40 | 82-83 | 0.8 | 70.0097 | 280320 | 1627120.4825 | 19625123.1592
Wood Products | 74.14% | >50 | 60 | 80-83 | 0.8 | 39.7172 | 420480 | 1193875.2006 | 16700271.1859
Chemicals | 68.18% | >50 | 60 | 80-83 | 0.85 | 73.6407 | 446760 | 2557335.3031 | 32899732.0831
Oil and Gas | 70% | 50-100 | 65 | 77-82 | 0.85 | 292.6725 | 483990 | 10724972.4852 | 141650579.9938
Carbon Intensity of Natural Gas (MTCO2e/MMBTU) | Hours per Year
0.053 | 8760
References | DOE 2010 | [6 empty] | Einstein et al., 2001 | DOE 2002 | ARB 2009
Sub-Sector | NAICS Code | Total Fuel (MMBTU) | Fuel to Boilers for Steam (MMBTU) | Fuel to CHP for Steam (MMBTU) | Fuel to Process Heating (MMBTU) | Fuel Used for Steam (percent) | Fuel Used for Process Heating (percent) | Fuel Used for Steam (percent) | Fuel Used for Steam (percent) | Fuel Used for Steam (percent)
Manufacturing | 31-33 | 12281 | 2498 | 3162 | 5238 | 46.09% | 42.65% | 0 | 0 | 0
Aluminum | 3313 | 120 | 4 | 15 | 92 | 15.83% | 76.67% | 0 | 0 | 0
Cement | 327310 | 341 | 4 | 10 | 315 | 4.106% | 92.38% | 0 | 0 | 0
Chemicals | 325 | 2417 | 771 | 877 | 488 | 68.18% | 20.19% | 42% | 47% | 0
Computers and Electronics | 334, 335 | 87 | 27 | 0 | 27 | 31.03% | 31.03% | 0 | 0 | 0
Fabrication and Metals | 332 | 252 | 37 | 2 | 166 | 15.48% | 65.87% | 0 | 0 | 0
Food and Beverage | 311, 312 | 1009 | 458 | 187 | 260 | 63.92% | 25.77% | 57% | 0 | 0
Wood Products | 321, 322 | 2378 | 411 | 1352 | 386 | 74.14% | 16.23% | 81% | 84% | 0
Foundries | 3315 | 100 | 6 | 0 | 69 | 6% | 69% | 0 | 0 | 0
Glass | 3272, 327993 | 267 | 15 | 0 | 238 | 5.618% | 89.14% | 0 | 0 | 0
Machinery | 333 | 93 | 18 | 6 | 26 | 25.81% | 27.96% | 0 | 0 | 0
Petroleum | 324110 | 3020 | 409 | 609 | 1890 | 33.71% | 62.58% | 23% | 51% | 0
Iron and Steel | 3311, 3312 | 994 | 67 | 50 | 758 | 11.77% | 76.26% | 10% | 0 | 0
Textiles | 313, 316 | 171 | 86 | 16 | 51 | 59.65% | 29.82% | 0 | 0 | 0
Transportation Equipment | 336 | 276 | 50 | 7 | 77 | 20.65% | 27.9% | 0 | 0 | 0
Oil and Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70%
California Air Resources Board (ARB) (2009): Oil and Natural Gas Production, Processing, and Storage.
Einstein et al. (2001): Steam Systems in Industry: Energy Use and Energy Efficiency Improvement Potentials. Lawrence Berkeley National Laboratory.
U.S. Department of Energy (DOE) (2002): Steam System Opportunity Assessment for the Pulp and Paper, Chemical Manufacturing, and Petroleum Refining Industry.
U.S. Department of Energy (DOE) (2010): IAC Case Study Database. http://iac.rutgers.edu/database/

## CBE Total REDUX added
CBE Summary of CARB data Industrial Boiler Fuel Reduction (MMBTU) Statewide 2008 data
`
| 1. REPLACE BOILERS |  | 2. OPTIMIZE BOILERS |  | 3. FEEDWATER ECONOMIZR |  | TOTAL 1-3
Sub Sector | Replace Low Efficiency Boilers (Category 1) | Replace Medium Efficiency Boilers (Category 2) | Reduce Excess Air of Boilers (Category 1) | Reduce Excess Air of Boilers (Category 2) | Retrofit Boilers with Feedwater Economizer (Category 1) | Retrofit Boilers with Feedwater Economizer (Category 2)
Petroleum | 3339654.1129 | 3258199.1346 | 1500617.9147 | 900370.7488 | 667930.8226 | 400758.4936 | 10067531.2272
Food | 215397.6932 | 236447.267 | 132273.3301 | 79363.9981 | 103031.8966 | 61819.138 | 828333.3229
Wood Products | 250504.0678 | 244394.2125 | 112559.8278 | 67535.8967 | 87676.4237 | 52605.8542 | 815276.2827
Chemicals | 493495.9812 | 481459.4939 | 221744.1942 | 133046.5165 | 98699.1962 | 59219.5177 | 1487664.8999
Oil and Gas | 3035369.5713 | 2072935.317 | 954724.9092 | 572834.9455 | 743665.545 | 446199.327 | 7825729.6149
Total | 7334421.4265 | 6293435.4249 | 2921920.176 | 1753152.1056 | 1701003.8841 | 1020602.3305 | 21024535.3476
| 4. AIR PREHEATER |  | 5. BLOWDOWN PRCTCS |  | 6. BLOWDOWN HEAT RECOV |  | TOTAL 4-6
Sub Sector | Retrofit Boilers with Air Preheaters (Category 1) | Retrofit Boilers with Air Preheaters (Category 2) | Blowdown Reduction With Controls (Category 1) | Blowdown Reduction with Feedwater Cleanup (Category 2) | Blowdown Heat Recovery (Category 1) | Blowdown Heat Recovery (Category 2)
Petroleum | 166982.7056 | 100189.6234 | 189247.0664 | 567741.1992 | 333965.4113 | 200379.2468 | 1558505.2527
Food | 17662.6108 | 10597.5665 | 24138.9015 | 72416.7045 | 29437.6847 | 17662.6108 | 171916.0789
Wood Products | 15030.2441 | 9018.1464 | 20541.3336 | 61624.0007 | 25050.4068 | 15030.2441 | 146294.3756
Chemicals | 31254.7455 | 18752.8473 | 27964.7723 | 83894.3168 | 49349.5981 | 29609.7589 | 240826.0388
Oil and Gas | 127485.522 | 76491.3132 | 174230.2134 | 522690.6402 | 212475.87 | 127485.522 | 1240859.0807
Total | 358415.828 | 215049.4968 | 436122.2871 | 1308366.8613 | 650278.9709 | 390167.3826 | 3358400.8268
| 7. OPTIMIZE STEAM QUAL. |  | 8. OPTIMIZE CONDENS RECOV |  | 9. MINIMIZE VENTED STEAM |  | TOTAL 7-9
Sub Sector | Optimize Steam Quality (Category 1) | Optimize Steam Quality (Category 2) | Optimize Condensate Recovery (Category 1) | Optimize Condensate Recovery (Category 2) | Minimize Vented Steam (Category 1) | Minimize Vented Steam (Category 2)
Petroleum | 129133.2924 | 77479.9754 | 178114.886 | 106868.9316 | 228209.6977 | 136925.8186 | 856732.6018
Food | 22176.3892 | 13305.8335 | 15700.0985 | 9420.0591 | 31400.1971 | 18840.1182 | 110842.6956
Wood Products | 18871.3064 | 11322.7839 | 13360.2169 | 8016.1302 | 26720.4339 | 16032.2603 | 94323.1317
Chemicals | 19081.8446 | 11449.1068 | 26319.7857 | 15791.8714 | 33722.2254 | 20233.3352 | 126598.1691
Oil and Gas | 160065.1554 | 96039.0932 | 113320.464 | 67992.2784 | 216017.1345 | 129610.2807 | 783044.4062
Total | 349327.988 | 209596.7928 | 346815.4512 | 208089.2707 | 536069.6885 | 321641.8131 | 1971541.0043
| 10 INSULATION MAINT. |  | 11 STEAM TRAP MAINT. |  | 12 STEAM LEAK MAINT. |  | TOTAL 10-12
Sub Sector | Insulation Maintenance (Category 1) | Insulation Maintenance (Category 2) | Steam Trap Maintenance (Category 1) | Steam Trap Maintenance (Category 2) | Steam Leak Maintenance (Category 1) | Steam Leak Maintenance (Category 2)
Petroleum | 3117010.5054 | 834913.5282 | 3339654.1129 | 3339654.1129 | 1113218.0376 | 667930.8226 | 12412381.1197
Food | 274751.7242 | 73594.2118 | 294376.8474 | 294376.8474 | 98125.6158 | 58875.3695 | 1094100.6161
Wood Products | 233803.7966 | 62626.0169 | 250504.0678 | 250504.0678 | 83501.3559 | 50100.8136 | 931040.1186
Chemicals | 460596.2492 | 123373.9953 | 493495.9812 | 493495.9812 | 164498.6604 | 98699.1962 | 1834160.0636
Oil and Gas | 1983108.1199 | 531189.675 | 2124758.6999 | 2124758.6999 | 708252.9 | 424951.74 | 7897019.8347
Total | 6069270.3953 | 1625697.4273 | 6502789.7093 | 6502789.7093 | 2167596.5698 | 1300557.9419 | 24168701.7528
GRAND TOTAL | [6 empty] | 50523178.9314
Total from Petroleum, Chemicals, Oil & Gas (Excluding Food & Wood Products) | [5 empty] | Million BTUs | 46331052.3094
(Annual)
To calculate NOx & CO CoPollutants, using AP42 Emission Factors:
AP42 - 1.4 Natural Gas Combustion Emission Factors:
| AP42 Factors: |  |  | Converting AP42 to lb/MMBTU assuming natural gas,
at 1020 MMbtu/MMscf:
Large Wall-Fired Boilers (>100) | Nox, (lb/ million scf) | CO, (lb/ million scf) | CO2 lbs/million scf | Nox, (lb/ MMBTU) | CO, (lb/ MMBTU | TCO2 /MMBTU
Uncontrolled (Pre-NSPS)c | 280 | 84 | 120000 | 0.27451 | 0.082353 | 0.053476
Uncontrolled (Post-NSPS)c | 190 | 84 | 120000 | 0.18627 | 0.082353 | 0.053476
Controlled - Low NOx burners | 140 | 84 | 120000 | 0.13725 | 0.082353 | 0.053476
Controlled - Flue gas recirculation | 100 | 84 | 120000 | 0.098039 | 0.082353 | 0.053476
Natural gas - (lbs/MM scf) /(1020 MM btu/MM scf) = lbs/MMBTU
For comparison SCAQMD refinery inventory:
Estimations assume Category 1 similar to Pre-NSPS Emission Factors
and Category 2 similar to Category 2 Post-NSPS Emission Factors
NOX CO-POLLUTANT REDUCTIONS USING AP42 EMISSION FACTORS | [5 empty] | tons/day
| 1. REPLACE BOILERS |  | 2. OPTIMIZE BOILERS |  | 3. FEEDWATER ECONOMIZR |  | TOTAL 1-3
Sub Sector | Replace Low Efficiency Boilers (Cat. 1) * | Replace Medium Efficiency Boilers (Cat. 2) ** | Reduce Excess Air of Boilers (Cat. 1) * | Reduce Excess Air of Boilers (Cat. 2) ** | Retrofit Boilers with Feedwater Economizer (Cat. 1) * | Retrofit Boilers with Feedwater Economizer (Cat. 2) **
Petroleum | 1.2558 | 0.8314 | 0.56429 | 0.22975 | 0.25117 | 0.10226 | 3.2347
Food | 0.080998 | 0.060334 | 0.04974 | 0.020251 | 0.038744 | 0.015774 | 0.26584
Wood Products | 0.0942 | 0.062362 | 0.042327 | 0.017233 | 0.03297 | 0.013423 | 0.26252
Chemicals | 0.18557 | 0.12285 | 0.083385 | 0.03395 | 0.037115 | 0.015111 | 0.47799
Oil and Gas | 1.1414 | 0.52895 | 0.35902 | 0.14617 | 0.27965 | 0.11386 | 2.5691
Total | 2.758 | 1.6059 | 1.0988 | 0.44735 | 0.63965 | 0.26043 | 6.8101
| 4. AIR PREHEATER |  | 5. BLOWDOWN PRCTCS |  | 6. BLOWDOWN HEAT RECOV |  | TOTAL 4-6
Sub Sector | Retrofit Boilers with Air Pre-heaters (Cat. 1) * | Retrofit Boilers with Air Preheaters (Cat. 2) * | Blowdown Reduction With Controls (Cat. 1) * | Blowdown Reduction w/Feedwater Cleanup (Cat. 2) ** | Blowdown Heat Recovery (Cat. 1) * | Blowdown Heat Recovery (Cat. 2) **
Petroleum | 0.062792 | 0.025565 | 0.071165 | 0.14487 | 0.12558 | 0.051131 | 0.48111
Food | 0.0066419 | 0.0027042 | 0.0090772 | 0.018479 | 0.01107 | 0.004507 | 0.052479
Wood Products | 0.005652 | 0.0023012 | 0.0077244 | 0.015725 | 0.00942 | 0.0038353 | 0.044657
Chemicals | 0.011753 | 0.0047852 | 0.010516 | 0.021407 | 0.018557 | 0.0075555 | 0.074574
Oil and Gas | 0.04794 | 0.019518 | 0.065518 | 0.13338 | 0.0799 | 0.032531 | 0.37878
Total | 0.13478 | 0.054874 | 0.164 | 0.33386 | 0.24453 | 0.099559 | 1.0316
| 7. OPTIMIZE STEAM QUAL. |  | 8. OPTIMIZE COND RECOV |  | 9. MINIMIZE VENTD STEAM |  | TOTAL 7-9
Sub Sector | Optimize Steam Quality (Cat. 1)* | Optimize Steam Quality (Cat. 2)** | Optimize Condensate Recovery (Cat. 1)* | Optimize Condensate Recovery (Cat. 2)** | Minimize Vented Steam (Cat. 1)* | Minimize Vented Steam (Cat. 2)**
Petroleum | 0.048559 | 0.019771 | 0.066978 | 0.02727 | 0.085816 | 0.034939 | 0.28333
Food | 0.0083392 | 0.0033953 | 0.0059039 | 0.0024037 | 0.011808 | 0.0048074 | 0.036657
Wood Products | 0.0070964 | 0.0028892 | 0.005024 | 0.0020455 | 0.010048 | 0.004091 | 0.031194
Chemicals | 0.0071756 | 0.0029215 | 0.0098973 | 0.0040296 | 0.012681 | 0.005163 | 0.041868
Oil and Gas | 0.060191 | 0.024506 | 0.042613 | 0.01735 | 0.081231 | 0.033073 | 0.25896
Total | 0.13136 | 0.053483 | 0.13042 | 0.053098 | 0.20158 | 0.082074 | 0.65202
| 10 INSULATION MAINT. |  | 11 STEAM TRAP MAINT. |  | 12 STEAM LEAK MAINT. |  | TOTAL 10-12
Sub Sector | Insulation Maint. (Cat. 1)* | Insulation Maint. (Cat. 2)** | Steam Trap Maint. (Cat. 1)* | Steam Trap Maint. (Cat. 2)** | Steam Leak Maint. (Cat. 1)* | Steam Leak Maint. (Cat. 2)**
Petroleum | 1.1721 | 0.21305 | 1.2558 | 0.85218 | 0.41862 | 0.17044 | 4.0822
Food | 0.10332 | 0.018779 | 0.1107 | 0.075116 | 0.036899 | 0.015023 | 0.35983
Wood Products | 0.08792 | 0.01598 | 0.0942 | 0.063921 | 0.0314 | 0.012784 | 0.30621
Chemicals | 0.1732 | 0.031481 | 0.18557 | 0.12593 | 0.061858 | 0.025185 | 0.60323
Oil and Gas | 0.74573 | 0.13554 | 0.799 | 0.54218 | 0.26633 | 0.10844 | 2.5972
Total | 2.2823 | 0.41483 | 2.4453 | 1.6593 | 0.8151 | 0.33186 | 7.9487
* using uncontrolled pre NSPS emission factor |  |  |  | ** using uncontrolled post NSPS emisssion factor
GRAND TOTAL | [6 empty] | 16.4425
Total from Petroleum, Chemicals, Oil & Gas (Excluding Food & Wood Products) | [5 empty] | Tons per day | 15.0831
CO CO-POLLUTANT REDUCTIONS USING AP42 EMISSION FACTORS
| 1. REPLACE BOILERS |  | 2. OPTIMIZE BOILERS |  | 3. FEEDWATER ECONOMIZR |  | TOTAL 1-3
Sub Sector | Replace Low Efficiency Boilers (Cat. 1) * | Replace Medium Efficiency Boilers (Cat. 2) ** | Reduce Excess Air of Boilers (Cat. 1) * | Reduce Excess Air of Boilers (Cat. 2) ** | Retrofit Boilers with Feedwater Economizer (Cat. 1) * | Retrofit Boilers with Feedwater Economizer (Cat. 2) **
Petroleum | 0.37675 | 0.36756 | 0.16929 | 0.10157 | 0.075351 | 0.04521 | 1.1357
Food | 0.024299 | 0.026674 | 0.014922 | 0.0089532 | 0.011623 | 0.006974 | 0.093446
Wood Products | 0.02826 | 0.027571 | 0.012698 | 0.0076189 | 0.009891 | 0.0059346 | 0.091973
Chemicals | 0.055672 | 0.054315 | 0.025015 | 0.015009 | 0.011134 | 0.0066807 | 0.16783
Oil and Gas | 0.34243 | 0.23385 | 0.1077 | 0.064623 | 0.083895 | 0.050337 | 0.88284
Total | 0.82741 | 0.70998 | 0.32963 | 0.19778 | 0.19189 | 0.11514 | 2.3718
| 4. AIR PREHEATER |  | 5. BLOWDOWN PRCTCS |  | 6. BLOWDOWN HEAT RECOV |  | TOTAL 4-6
Sub Sector | Retrofit Boilers with Air Pre-heaters (Cat. 1) * | Retrofit Boilers with Air Preheaters (Cat. 2) * | Blowdown Reduction With Controls (Cat. 1) * | Blowdown Reduction w/Feedwater Cleanup (Cat. 2) ** | Blowdown Heat Recovery (Cat. 1) * | Blowdown Heat Recovery (Cat. 2) **
Petroleum | 0.018838 | 0.011303 | 0.021349 | 0.064048 | 0.037675 | 0.022605 | 0.17582
Food | 0.0019926 | 0.0011955 | 0.0027232 | 0.0081695 | 0.0033209 | 0.0019926 | 0.019394
Wood Products | 0.0016956 | 0.0010174 | 0.0023173 | 0.0069519 | 0.002826 | 0.0016956 | 0.016504
Chemicals | 0.0035259 | 0.0021156 | 0.0031548 | 0.0094643 | 0.0055672 | 0.0033403 | 0.027168
Oil and Gas | 0.014382 | 0.0086292 | 0.019655 | 0.058966 | 0.02397 | 0.014382 | 0.13998
Total | 0.040434 | 0.02426 | 0.0492 | 0.1476 | 0.073359 | 0.044016 | 0.37887
| 7. OPTIMIZE STEAM QUAL. |  | 8. OPTIMIZE COND RECOV |  | 9. MINIMIZE VENTD STEAM |  | TOTAL 7-9
Sub Sector | Optimize Steam Quality (Cat. 1)* | Optimize Steam Quality (Cat. 2)** | Optimize Condensate Recovery (Cat. 1)* | Optimize Condensate Recovery (Cat. 2)** | Minimize Vented Steam (Cat. 1)* | Minimize Vented Steam (Cat. 2)**
Petroleum | 0.014568 | 0.0087407 | 0.020094 | 0.012056 | 0.025745 | 0.015447 | 0.09665
Food | 0.0025018 | 0.0015011 | 0.0017712 | 0.0010627 | 0.0035423 | 0.0021254 | 0.012504
Wood Products | 0.0021289 | 0.0012773 | 0.0015072 | 0.00090432 | 0.0030144 | 0.0018086 | 0.010641
Chemicals | 0.0021527 | 0.0012916 | 0.0029692 | 0.0017815 | 0.0038043 | 0.0022826 | 0.014282
Oil and Gas | 0.018057 | 0.010834 | 0.012784 | 0.0076704 | 0.024369 | 0.014622 | 0.088337
Total | 0.039408 | 0.023645 | 0.039125 | 0.023475 | 0.060475 | 0.036285 | 0.22241
| 10 INSULATION MAINT. |  | 11 STEAM TRAP MAINT. |  | 12 STEAM LEAK MAINT. |  | TOTAL 10-12
Sub Sector | Insulation Maint. (Cat. 1)* | Insulation Maint. (Cat. 2)** | Steam Trap Maint. (Cat. 1)* | Steam Trap Maint. (Cat. 2)** | Steam Leak Maint. (Cat. 1)* | Steam Leak Maint. (Cat. 2)**
Petroleum | 0.35164 | 0.094188 | 0.37675 | 0.37675 | 0.12558 | 0.075351 | 1.4003
Food | 0.030995 | 0.0083023 | 0.033209 | 0.033209 | 0.01107 | 0.0066419 | 0.12343
Wood Products | 0.026376 | 0.007065 | 0.02826 | 0.02826 | 0.00942 | 0.005652 | 0.10503
Chemicals | 0.051961 | 0.013918 | 0.055672 | 0.055672 | 0.018557 | 0.011134 | 0.20692
Oil and Gas | 0.22372 | 0.059925 | 0.2397 | 0.2397 | 0.0799 | 0.04794 | 0.89088
Total | 0.68469 | 0.1834 | 0.73359 | 0.73359 | 0.24453 | 0.14672 | 2.7265
* using uncontrolled pre NSPS emission factor |  |  |  | ** using uncontrolled post NSPS emisssion factor
GRAND TOTAL | [6 empty] | 5.6996
Total from Petroleum, Chemicals, Oil & Gas (Excluding Food & Wood Products) | [5 empty] | Tons per day | 5.2267

## Replace Boiler
Sub-Sector | Percent of Fuel Use By Steam | Assumptions |  |  |  | Calculations
|  | Boiler Size Category (MMBTU/hr) | Unit Size (MMBTU/hr) | Efficiency (percent) | Capacity Factor (staff estimate) (percent) | Total Number of Boilers | Fuel Use Per Unit (MMBTU/unit) | 2008 Emissions (MTCO2e) | Amount of Natural Gas to Produce Steam (MMBTU)
Petroleum | 33.71% | >60 | 100 | 80-83 | 0.9 | 282.3993 | 788400 | 35006223.7928 | 222643607.529
Food | 63.92% | 10-100 | 40 | 82-83 | 0.8 | 70.0097 | 280320 | 1627120.4825 | 19625123.1592
Wood Products | 74.14% | >50 | 60 | 80-83 | 0.8 | 39.7172 | 420480 | 1193875.2006 | 16700271.1859
Chemicals | 68.18% | >50 | 60 | 80-83 | 0.85 | 73.6407 | 446760 | 2557335.3031 | 32899732.0831
Oil and Gas | 70% | 50-100 | 65 | 77-82 | 0.85 | 292.6725 | 483990 | 10724972.4852 | 141650579.9938
Sub-Sector | Replace Low Efficiency Boilers (Category 1) | [6 empty] | Replace Medium Efficiency Boilers (Category 2)
| Feasibility (percent) | Efficiency of Old Unit (percent) | Efficiency of New Unit (percent) | Efficiency Increase From Low Efficiency Unit (percent) | Number of Units | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e) | Feasibility (percent) | Efficiency of Old Unit (percent) | Efficiency of New Unit (percent) | Efficiency Increase From Med Efficiency Unit (percent) | Number of Units | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e)
Petroleum | 15% | 80% | 88% | 10% | 42.3599 | 3339654.1129 | 177001.668 | 20% | 82% | 88% | 7.317% | 56.4799 | 3258199.1346 | 172684.5541
Food | 15% | 82% | 88% | 7.317% | 10.5015 | 215397.6932 | 11416.0777 | 20% | 83% | 88% | 6.024% | 14.0019 | 236447.267 | 12531.7051
Wood Products | 15% | 80% | 88% | 10% | 5.9576 | 250504.0678 | 13276.7156 | 20% | 82% | 88% | 7.317% | 7.9434 | 244394.2125 | 12952.8933
Chemicals | 15% | 80% | 88% | 10% | 11.0461 | 493495.9812 | 26155.287 | 20% | 82% | 88% | 7.317% | 14.7281 | 481459.4939 | 25517.3532
Oil and Gas | 15% | 77% | 88% | 14.29% | 43.9009 | 3035369.5713 | 160874.5873 | 20% | 82% | 88% | 7.317% | 58.5345 | 2072935.317 | 109865.5718
Total | [5 empty] | 7334421.4265 | 388724.3356 | [5 empty] | 6293435.4249 | 333552.0775 | 0
Unit Size (MMBTU/hr) | Unit Cost for Size | Interest Rate | Years | Annuity Factor | 2020 Price of Fuel ($/MMBTU) | Carbon Intensity Natural Gas (MTCO2e/MMBTU) | Hours per Year
50 | 1500000 | 30% | 20 | 0.30159 | 7.69 | 0.053 | 8760
Sub-Sector | Replace Low Efficiency Boilers (Category 1) |  |  |  | Replace Medium Efficiency Boilers (Category 2)
| Price per Unit | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e) | Price per Unit | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e)
Petroleum | 3000000 | 38325566.2211 | 25681940.1285 | 71.4322 | 3000000 | 51100754.9614 | 25055551.3448 | 150.8253
Food | 1200000 | 3800522.1047 | 1656408.2608 | 187.8153 | 1200000 | 5067362.8063 | 1818279.4831 | 259.2691
Wood Products | 1800000 | 3234107.0821 | 1926376.2813 | 98.4981 | 1800000 | 4312142.7762 | 1879391.4939 | 187.8153
Chemicals | 1800000 | 5996451.0739 | 3794984.0958 | 84.1691 | 1800000 | 7995268.0985 | 3702423.5081 | 168.2324
Oil and Gas | 1950000 | 25817862.9047 | 23341992.0033 | 15.3901 | 1950000 | 34423817.2063 | 15940872.5876 | 168.2324
Total |  | 77174509.3865 | 56401700.7696 |  |  | 102899345.8487 | 48396518.4175
JM ADDED:
Convert to lb/btu assuming natural gas about 1020 btu/scf
AP42: | Large Wall-Fired Boilers (>100) | Nox, (lb/ million scf) | CO, (lb/ million scf) | CO2 lbs/million scf | Nox, (lb/ MMBTU) | CO, (lb/ MMBTU | TCO2 /MMBTU
1.4 Natural Gas Combustion | Uncontrolled (Pre-NSPS)c | 280 | 84 | 120000 | 0.27451 | 0.082353 | 0.053476
| Uncontrolled (Post-NSPS)c | 190 | 84 | 120000 | 0.18627 | 0.082353 | 0.053476
| Controlled - Low NOx burners | 140 | 84 | 120000 | 0.13725 | 0.082353 | 0.053476
| Controlled - Flue gas recirculation | 100 | 84 | 120000 | 0.098039 | 0.082353 | 0.053476
| Natural gas: | (lbs/MM scf) /(1020 MM btu/MM scf) = lbs/MMBTU
|  | #VALUE! | 0 | #VALUE! | 0
|  | #VALUE! | 0 | #VALUE! | 0
|  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0
|  |  | #VALUE! |  | #VALUE!

## Optimize Boiler
Sub-Sector | Percent of Fuel Use By Steam | Assumptions |  |  |  | Calculations
|  | Boiler Size Category (MMBTU/hr) | Unit Size (MMBTU/hr) | Efficiency (percent) | Capacity Factor (staff estimate) (percent) | Total Number of Boilers | Fuel Use per Unit (MMBTU) | 2008 Emissions (MTCO2e) | Amount of Natural Gas to Produce Steam (MMBTU)
Petroleum | 33.71% | >60 | 100 | 80-83 | 0.9 | 282.3993 | 788400 | 35006223.7928 | 222643607.529
Food | 63.92% | 10-100 | 40 | 82-83 | 0.8 | 70.0097 | 280320 | 1627120.4825 | 19625123.1592
Wood Products | 74.14% | >50 | 60 | 80-83 | 0.8 | 39.7172 | 420480 | 1193875.2006 | 16700271.1859
Chemicals | 68.18% | >50 | 60 | 80-83 | 0.85 | 73.6407 | 446760 | 2557335.3031 | 32899732.0831
Oil and Gas | 70% | 50-100 | 65 | 77-82 | 0.85 | 292.6725 | 483990 | 10724972.4852 | 141650579.9938
Sub-Sector | Reduce Excess Air of Boilers (Category 1) |  |  |  |  | Reduce Excess Air of Boilers (Category 2)
| Feasibility (percent) | Efficiency Increase (percent) | Number of Units | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e) | Feasibility (percent) | Efficiency Increase (percent) | Number of Units | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e)
Petroleum | 33.7% | 2% | 95.1686 | 1500617.9147 | 79532.7495 | 40.44% | 1% | 114.2023 | 900370.7488 | 47719.6497
Food | 33.7% | 2% | 23.5933 | 132273.3301 | 7010.4865 | 40.44% | 1% | 28.3119 | 79363.9981 | 4206.2919
Wood Products | 33.7% | 2% | 13.3847 | 112559.8278 | 5965.6709 | 40.44% | 1% | 16.0616 | 67535.8967 | 3579.4025
Chemicals | 33.7% | 2% | 24.8169 | 221744.1942 | 11752.4423 | 40.44% | 1% | 29.7803 | 133046.5165 | 7051.4654
Oil and Gas | 33.7% | 2% | 98.6306 | 954724.9092 | 50600.4202 | 40.44% | 1% | 118.3568 | 572834.9455 | 30360.2521
Total |  |  |  | 2921920.176 | 154861.7693 |  |  |  | 1753152.1056 | 92917.0616
Interest Rate | Years | Annuity Factor | 2020 Price of Fuel ($/MMBTU) | Carbon Intensity Natural Gas (MTCO2e/MMBTU) | Hours per Year
0.3 | 20 | 0.30159 | 7.69 | 0.053 | 8760
Sub-Sector | Reduce Excess Air of Boilers (Category 1) |  |  |  | Reduce Excess Air of Boilers (Category 2)
| Price Per Unit | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e) | Price Per Unit1 | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e)
Petroleum | 121255.92 | 3480237.7862 | 11539751.7644 | -101.3358 | 181883.88 | 5220356.6793 | 6923851.0586 | -35.698
Food | 43113.216 | 306768.7231 | 1017181.9084 | -101.3358 | 64669.824 | 460153.0846 | 610309.1451 | -35.698
Wood Products | 64669.824 | 261049.1065 | 865585.0757 | -101.3358 | 97004.736 | 391573.6598 | 519351.0454 | -35.698
Chemicals | 68711.688 | 514269.8325 | 1705212.8537 | -101.3358 | 103067.532 | 771404.7488 | 1023127.7122 | -35.698
Oil and Gas | 74437.662 | 2214201.0112 | 7341834.5514 | -101.3358 | 111656.493 | 3321301.5168 | 4405100.7309 | -35.698
Total |  | 6776526.4595 | 22469566.1537 |  |  | 10164789.6892 | 13481739.6922
1 For Category 2, staff assumed a 50 percent greater cost than Category 1
JM ADDED:
Convert to lb/btu assuming natural gas about 1020 btu/scf
AP42: | Large Wall-Fired Boilers (>100) | Nox, (lb/ million scf) | CO, (lb/ million scf) | CO2 lbs/million scf | Nox, (lb/ MMBTU) | CO, (lb/ MMBTU | TCO2 /MMBTU
1.4 Natural Gas Combustion | Uncontrolled (Pre-NSPS)c | 280 | 84 | 120000 | 0.27451 | 0.082353 | 0.053476
| Uncontrolled (Post-NSPS)c | 190 | 84 | 120000 | 0.18627 | 0.082353 | 0.053476
| Controlled - Low NOx burners | 140 | 84 | 120000 | 0.13725 | 0.082353 | 0.053476
| Controlled - Flue gas recirculation | 100 | 84 | 120000 | 0.098039 | 0.082353 | 0.053476
| Natural gas: | (lbs/MM scf) /(1020 MM btu/MM scf) = lbs/MMBTU

## Feedwater Economizer
Sub-Sector | Percent of Fuel Use By Steam | Assumptions |  |  |  | Calculations
|  | Boiler Size Category (MMBTU/hr) | Unit Size (MMBTU/hr) | Efficiency (percent) | Capacity Factor (staff estimate) (percent) | Total Number of Boilers | Fuel Use per Unit (MMBTU) | 2008 Emissions (MTCO2e) | Amount of Natural Gas to Produce Steam (MMBTU)
Petroleum | 33.71% | >60 | 100 | 80-83 | 0.9 | 282.3993 | 788400 | 35006223.7928 | 222643607.529
Food | 63.92% | 10-100 | 40 | 82-83 | 0.8 | 70.0097 | 280320 | 1627120.4825 | 19625123.1592
Wood Products | 74.14% | >50 | 60 | 80-83 | 0.8 | 39.7172 | 420480 | 1193875.2006 | 16700271.1859
Chemicals | 68.18% | >50 | 60 | 80-83 | 0.85 | 73.6407 | 446760 | 2557335.3031 | 32899732.0831
Oil and Gas | 70% | 50-100 | 65 | 77-82 | 0.85 | 292.6725 | 483990 | 10724972.4852 | 141650579.9938
Sub-Sector | Retrofit Boilers with Feedwater Economizer (Category 1) |  |  |  |  | Retrofit Boilers with Feedwater Economizer (Category 2)
| Feasibility (percent) | Efficiency Increase (percent) | Number of Units | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e) | Feasibility (percent) | Efficiency Increase (percent) | Number of Units | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e)
Petroleum | 15% | 2% | 42.3599 | 667930.8226 | 35400.3336 | 18% | 1% | 50.8319 | 400758.4936 | 21240.2002
Food | 15% | 3.5% | 10.5015 | 103031.8966 | 5460.6905 | 18% | 1.75% | 12.6017 | 61819.138 | 3276.4143
Wood Products | 15% | 3.5% | 5.9576 | 87676.4237 | 4646.8505 | 18% | 1.75% | 7.1491 | 52605.8542 | 2788.1103
Chemicals | 15% | 2% | 11.0461 | 98699.1962 | 5231.0574 | 18% | 1% | 13.2553 | 59219.5177 | 3138.6344
Oil and Gas | 15% | 3.5% | 43.9009 | 743665.545 | 39414.2739 | 18% | 1.75% | 52.6811 | 446199.327 | 23648.5643
Total |  |  |  | 1701003.8841 | 90153.2059 |  |  |  | 1020602.3305 | 54091.9235
Unit Size (MMBTU/hr) | Unit Cost for Size | Interest Rate | Years | Annuity Factor | 2020 Price of Fuel ($/MMBTU) | Carbon Intensity Natural Gas (MTCO2e/MMBTU) | Hours per Year
50 | 250000 | 30% | 20 | 0.30159 | 7.6851 | 0.053 | 8760
Sub-Sector | Retrofit Boilers with Feedwater Economizer (Category 1) |  |  |  | Retrofit Boilers with Feedwater Economizer (Category 2)
| Price per Unit | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e) | Price per Unit | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e)
Petroleum | 500000 | 6387594.3702 | 5133115.1647 | 35.4369 | 500000 | 6387594.3702 | 3079869.0988 | 155.7295
Food | 200000 | 633420.3508 | 791810.4285 | -29.0055 | 200000 | 633420.3508 | 475086.2571 | 48.3254
Wood Products | 300000 | 539017.847 | 673802.084 | -29.0055 | 300000 | 539017.847 | 404281.2504 | 48.3254
Chemicals | 300000 | 999408.5123 | 758513.1931 | 46.051 | 300000 | 999408.5123 | 455107.9159 | 173.4196
Oil and Gas | 325000 | 4302977.1508 | 5715144.0796 | -35.8288 | 325000 | 4302977.1508 | 3429086.4478 | 36.9532
Total |  | 12862418.2311 | 13072384.9498 |  |  | 12862418.2311 | 7843430.9699

## Air Preheater
Sub-Sector | Percent of Fuel Use By Steam | Assumptions |  |  |  | Calculations
|  | Boiler Size Category (MMBTU/hr) | Unit Size (MMBTU/hr) | Efficiency (percent) | Capacity Factor (staff estimate) (percent) | Total Number of Boilers | Fuel Use per Unit (MMBTU) | 2008 Emissions (MTCO2e) | Amount of Natural Gas to Produce Steam (MMBTU)
Petroleum | 33.71% | >60 | 100 | 80-83 | 0.9 | 282.3993 | 788400 | 35006223.7928 | 222643607.529
Food | 63.92% | 10-100 | 40 | 82-83 | 0.8 | 70.0097 | 280320 | 1627120.4825 | 19625123.1592
Wood Products | 74.14% | >50 | 60 | 80-83 | 0.8 | 39.7172 | 420480 | 1193875.2006 | 16700271.1859
Chemicals | 68.18% | >50 | 60 | 80-83 | 0.85 | 73.6407 | 446760 | 2557335.3031 | 32899732.0831
Oil and Gas | 70% | 50-100 | 65 | 77-82 | 0.85 | 292.6725 | 483990 | 10724972.4852 | 141650579.9938
Sub-Sector | Retrofit Boilers with Air Preheaters (Category 1) |  |  |  |  | Retrofit Boilers with Air Preheaters (Category 2)
| Feasibility (percent) | Efficiency Increase (percent) | Number of Units | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e) | Feasibility (percent) | Efficiency Increase (percent) | Number of Units | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e)
Petroleum | 5% | 1.5% | 14.12 | 166982.7056 | 8850.0834 | 6% | 0.75% | 16.944 | 100189.6234 | 5310.05
Food | 5% | 1.8% | 3.5005 | 17662.6108 | 936.1184 | 6% | 0.9% | 4.2006 | 10597.5665 | 561.671
Wood Products | 5% | 1.8% | 1.9859 | 15030.2441 | 796.6029 | 6% | 0.9% | 2.383 | 9018.1464 | 477.9618
Chemicals | 5% | 1.9% | 3.682 | 31254.7455 | 1656.5015 | 6% | 0.95% | 4.4184 | 18752.8473 | 993.9009
Oil and Gas | 5% | 1.8% | 14.6336 | 127485.522 | 6756.7327 | 6% | 0.9% | 17.5604 | 76491.3132 | 4054.0396
Total |  |  |  | 358415.828 | 18996.0389 |  |  |  | 215049.4968 | 11397.6233
Interest Rate | Years | Annuity Factor | 2020 Price of Fuel ($/MMBTU) | Carbon Intensity Natural Gas (MTCO2e/MMBTU) | Hours per Year
0.3 | 20 | 0.30159 | 7.6851 | 0.053 | 8760
Sub-Sector | Retrofit Boilers with Air Preheaters (Category 1) |  |  |  | Retrofit Boilers with Air Preheaters (Category 2)
| Price Per Unit | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e) | Price Per Unit | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e)
Petroleum | 181767.9852 | 774040.106 | 1283278.7912 | -57.5406 | 181767.9852 | 928848.1272 | 769967.2747 | 29.9208
Food | 93065.2084 | 98248.9949 | 135738.9306 | -40.0483 | 93065.2084 | 117898.7939 | 81443.3584 | 64.9053
Wood Products | 139597.8126 | 83606.3471 | 115508.9287 | -40.0483 | 139597.8126 | 100327.6166 | 69305.3572 | 64.9053
Chemicals | 169609.7266 | 188343.7829 | 240195.8445 | -31.3022 | 169609.7266 | 226012.5394 | 144117.5067 | 82.3976
Oil and Gas | 160682.8989 | 709143.4283 | 979738.9851 | -40.0483 | 160682.8989 | 850972.1139 | 587843.391 | 64.9053
Total |  | 1853382.6592 | 2754461.48 |  |  | 2224059.191 | 1652676.888

## Blowdown Practices
Sub-Sector | Percent of Fuel Use By Steam | Assumptions |  |  |  | Calculations
|  | Boiler Size Category (MMBTU/hr) | Unit Size (MMBTU/hr) | Efficiency (percent) | Capacity Factor (staff estimate) (percent) | Total Number of Boilers | Fuel Use Per Unit (MMBTU) | 2008 Emissions (MTCO2e) | Amount of Natural Gas to Produce Steam (MMBTU)
Petroleum | 33.71% | >60 | 100 | 80-83 | 0.9 | 282.3993 | 788400 | 35006223.7928 | 222643607.529
Food | 63.92% | 10-100 | 40 | 82-83 | 0.8 | 70.0097 | 280320 | 1627120.4825 | 19625123.1592
Wood Products | 74.14% | >50 | 60 | 80-83 | 0.8 | 39.7172 | 420480 | 1193875.2006 | 16700271.1859
Chemicals | 68.18% | >50 | 60 | 80-83 | 0.85 | 73.6407 | 446760 | 2557335.3031 | 32899732.0831
Oil and Gas | 70% | 50-100 | 65 | 77-82 | 0.85 | 292.6725 | 483990 | 10724972.4852 | 141650579.9938
Sub-Sector | Blowdown Reduction With Controls (Category 1) |  |  |  |  | Blowdown Reduction with Feedwater Cleanup (Category 2)
| Feasibility (percent) | Efficiency Increase (percent) | Number of Units | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e) | Feasibility (percent) | Efficiency Increase (percent) | Number of Units | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e)
Petroleum | 8.5% | 1% | 24.0039 | 189247.0664 | 10030.0945 | 12.75% | 2% | 36.0059 | 567741.1992 | 30090.2836
Food | 12.3% | 1% | 8.6112 | 24138.9015 | 1279.3618 | 18.45% | 2% | 12.9168 | 72416.7045 | 3838.0853
Wood Products | 12.3% | 1% | 4.8852 | 20541.3336 | 1088.6907 | 18.45% | 2% | 7.3278 | 61624.0007 | 3266.072
Chemicals | 8.5% | 1% | 6.2595 | 27964.7723 | 1482.1329 | 12.75% | 2% | 9.3892 | 83894.3168 | 4446.3988
Oil and Gas | 12.3% | 1% | 35.9987 | 174230.2134 | 9234.2013 | 18.45% | 2% | 53.9981 | 522690.6402 | 27702.6039
Total |  |  |  | 436122.2871 | 23114.4812 |  |  | 119.6378 | 1308366.8613 | 69343.4437
Interest Rate | Years | Annuity Factor | 2020 Price of Fuel ($/MMBTU) | Carbon Emissions of Natural Gas (MMTCO2e/MMBTU) | Hours per Year
0.3 | 20 | 0.30159 | 7.6851 | 0.053 | 8760
Sub-Sector | Blowdown Reduction With Controls (Category 1) |  |  |  | Blowdown Reduction with Feedwater Cleanup (Category 2)
| Price Per Unit | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e) | Price Per Unit | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e)
Petroleum | 181767.9852 | 1315868.1801 | 1454382.63 | -13.8099 | 484714.6272 | 5263472.7205 | 4363147.89 | 29.9208
Food | 64628.617 | 167842.033 | 185509.8718 | -13.8099 | 172342.9786 | 671368.1321 | 556529.6154 | 29.9208
Wood Products | 96942.9254 | 142827.5097 | 157862.2025 | -13.8099 | 258514.4678 | 571310.0387 | 473586.6076 | 29.9208
Chemicals | 103001.8583 | 194443.9863 | 214912.0714 | -13.8099 | 274671.6221 | 777775.9454 | 644736.2141 | 29.9208
Oil and Gas | 111585.3465 | 1211453.3566 | 1338976.6129 | -13.8099 | 297560.9239 | 4845813.4265 | 4016929.8388 | 29.9208
Total |  | 3032435.0658 | 3351643.3886 |  |  | 12129740.2632 | 10054930.1659

## Blowdown Heat Recovery
Sub-Sector | Percent of Fuel Use By Steam | Assumptions |  |  |  | Calculations
|  | Boiler Size Range (MMBTU/hr) | Boiler Size (MMBTU/hr) | Efficiency (percent) | Capacity Factor (staff estimate) (percent) | Total Numbers of Boilers | Fuel Use Per Unit (MMBTU) | 2008 Emissions (MTCO2e) | Amount of Natural Gas to Produce Steam (MMBTU)
Petroleum | 33.71% | >60 | 100 | 80-83 | 0.9 | 282.3993 | 788400 | 35006223.7928 | 222643607.529
Food | 63.92% | 10-100 | 40 | 82-83 | 0.8 | 70.0097 | 280320 | 1627120.4825 | 19625123.1592
Wood Products | 74.14% | >50 | 60 | 80-83 | 0.8 | 39.7172 | 420480 | 1193875.2006 | 16700271.1859
Chemicals | 68.18% | >50 | 60 | 80-83 | 0.85 | 73.6407 | 446760 | 2557335.3031 | 32899732.0831
Oil and Gas | 70% | 50-100 | 65 | 77-82 | 0.85 | 292.6725 | 483990 | 10724972.4852 | 141650579.9938
Sub-Sector | Blowdown Heat Recovery (Category 1) |  |  |  |  | Blowdown Heat Recovery (Category 2)
| Feasibility (percent) | Efficiency Increase (percent) | Number of Units | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e) | Feasibility (percent) | Efficiency Increase (percent) | Number of Units | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e)
Petroleum | 15% | 1% | 42.3599 | 333965.4113 | 17700.1668 | 18% | 0.5% | 50.8319 | 200379.2468 | 10620.1001
Food | 15% | 1% | 10.5015 | 29437.6847 | 1560.1973 | 18% | 0.5% | 12.6017 | 17662.6108 | 936.1184
Wood Products | 15% | 1% | 5.9576 | 25050.4068 | 1327.6716 | 18% | 0.5% | 7.1491 | 15030.2441 | 796.6029
Chemicals | 15% | 1% | 11.0461 | 49349.5981 | 2615.5287 | 18% | 0.5% | 13.2553 | 29609.7589 | 1569.3172
Oil and Gas | 15% | 1% | 43.9009 | 212475.87 | 11261.2211 | 18% | 0.5% | 52.6811 | 127485.522 | 6756.7327
Total |  |  |  | 650278.9709 | 34464.7855 |  |  |  | 390167.3826 | 20678.8713
Interest Rate | Years | Annuity Factor | 2020 Price of Fuel ($/MMBTU) | Carbon Emissions of Natural Gas (MMTCO2e/MMBTU) | Hours in Year
0.3 | 20 | 0.30159 | 7.6851 | 0.053 | 8760
Sub-Sector | Blowdown Heat Recovery (Category 1) |  |  |  | Blowdown Heat Recovery (Category 2)
| Price Per Unit | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e) | Price Per Unit | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e)
Petroleum | 121178.6568 | 1548080.2119 | 2566557.5823 | -57.5406 | 121178.6568 | 1548080.2119 | 1539934.5494 | 0.767
Food | 43085.7446 | 136456.9374 | 226231.551 | -57.5406 | 43085.7446 | 136456.9374 | 135738.9306 | 0.767
Wood Products | 64628.617 | 116119.9266 | 192514.8811 | -57.5406 | 64628.617 | 116119.9266 | 115508.9287 | 0.767
Chemicals | 68667.9055 | 228757.631 | 379256.5965 | -57.5406 | 68667.9055 | 228757.631 | 227553.9579 | 0.767
Oil and Gas | 74390.231 | 984921.4281 | 1632898.3085 | -57.5406 | 74390.231 | 984921.4281 | 979738.9851 | 0.767
Total |  | 3014336.1351 | 4997458.9195 |  |  | 3014336.1351 | 2998475.3517

## Optimize Steam Quality
Sub-Sector | Percent of Fuel Use By Steam | Calculations
|  | 2008 Emissions (MTCO2e) | Amount of Natural Gas to Produce Steam (MMBTU)
Petroleum | 33.71% | 35006223.7928 | 222643607.529
Food | 63.92% | 1627120.4825 | 19625123.1592
Wood Products | 74.14% | 1193875.2006 | 16700271.1859
Chemicals | 68.18% | 2557335.3031 | 32899732.0831
Oil and Gas | 70% | 10724972.4852 | 141650579.9938
Sub-Sector | Optimize Steam Quality (Category 1) |  |  |  | Optimize Steam Quality (Category 2)
| Feasibility (percent) | Efficiency Increase (percent) | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e) | Feasibility (percent) | Efficiency Increase (percent) | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e)
Petroleum | 5.8% | 1% | 129133.2924 | 6844.0645 | 6.96% | 0.5% | 77479.9754 | 4106.4387
Food | 11.3% | 1% | 22176.3892 | 1175.3486 | 13.56% | 0.5% | 13305.8335 | 705.2092
Wood Products | 11.3% | 1% | 18871.3064 | 1000.1792 | 13.56% | 0.5% | 11322.7839 | 600.1075
Chemicals | 5.8% | 1% | 19081.8446 | 1011.3378 | 6.96% | 0.5% | 11449.1068 | 606.8027
Oil and Gas | 11.3% | 1% | 160065.1554 | 8483.4532 | 13.56% | 0.5% | 96039.0932 | 5090.0719
Total |  |  | 349327.988 | 18514.3834 |  |  | 209596.7928 | 11108.63
Interest Rate | Years | Annuity Factor | 2020 Price of Fuel ($/MMBTU) | Carbon Emissions of Natural Gas (MMTCO2e/MMBTU) | Hours in Year
0.3 | 20 | 0.30159 | 7.6851 | 0.053 | 8760
Sub-Sector | Optimize Steam Quality (Category 1) |  |  |  | Optimize Steam Quality (Category 2)
| Total Capital Cost | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e) | Total Capital Cost | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e)
Petroleum | 1488603.3978 | 448943.2615 | 992402.2652 | -79.4059 | 1488603.3978 | 448943.2615 | 595441.3591 | -35.6752
Food | 255641.6526 | 77098.1696 | 170427.7684 | -79.4059 | 255641.6526 | 77098.1696 | 102256.661 | -35.6752
Wood Products | 217541.8157 | 65607.7585 | 145027.8771 | -79.4059 | 217541.8157 | 65607.7585 | 87016.7263 | -35.6752
Chemicals | 219968.826 | 66339.713 | 146645.884 | -79.4059 | 219968.826 | 66339.713 | 87987.5304 | -35.6752
Oil and Gas | 1845175.0886 | 556480.6069 | 1230116.7257 | -79.4059 | 1845175.0886 | 556480.6069 | 738070.0354 | -35.6752
Total |  | 1214469.5095 | 2684620.5204 |  |  | 1214469.5095 | 1610772.3122

## Optimize Condensate Recovery
Sub-Sector | Percent of Fuel Use By Steam | Calculations
|  | 2008 Emissions (MTCO2e) | Amount of Natural Gas to Produce Steam (MMBTU)
Petroleum | 33.71% | 35006223.7928 | 222643607.529
Food | 63.92% | 1627120.4825 | 19625123.1592
Wood Products | 74.14% | 1193875.2006 | 16700271.1859
Chemicals | 68.18% | 2557335.3031 | 32899732.0831
Oil and Gas | 70% | 10724972.4852 | 141650579.9938
Sub-Sector | Optimize Condensate Recovery (Category 1) |  |  |  | Optimize Condensate Recovery (Category 2)
| Feasibility (percent) | Efficiency Increase (percent) | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e) | Feasibility (percent) | Efficiency Increase (percent) | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e)
Petroleum | 20% | 0.4% | 178114.886 | 9440.089 | 24% | 0.2% | 106868.9316 | 5664.0534
Food | 20% | 0.4% | 15700.0985 | 832.1052 | 24% | 0.2% | 9420.0591 | 499.2631
Wood Products | 20% | 0.4% | 13360.2169 | 708.0915 | 24% | 0.2% | 8016.1302 | 424.8549
Chemicals | 20% | 0.4% | 26319.7857 | 1394.9486 | 24% | 0.2% | 15791.8714 | 836.9692
Oil and Gas | 20% | 0.4% | 113320.464 | 6005.9846 | 24% | 0.2% | 67992.2784 | 3603.5908
Total |  |  | 346815.4512 | 18381.2189 |  |  | 208089.2707 | 11028.7313
Interest Rate | Years | Annuity Factor | 2020 Price of Fuel ($/MMBTU) | Carbon Emissions of Natural Gas (MMTCO2e/MMBTU) | Hours per Year
0.3 | 20 | 0.30159 | 7.6851 | 0.053 | 8760
Sub-Sector | Optimize Condensate Recovery (Category 1) |  |  |  | Optimize Condensate Recovery (Category 2)
| Total Capital Cost | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e) | Total Capital Cost | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e)
Petroleum | 3422076.7764 | 1032053.4746 | 1368830.7106 | -35.6752 | 3422076.7764 | 1032053.4746 | 821298.4263 | 37.2092
Food | 301642.068 | 90971.2916 | 120656.8272 | -35.6752 | 301642.068 | 90971.2916 | 72394.0963 | 37.2092
Wood Products | 256686.5082 | 77413.2844 | 102674.6033 | -35.6752 | 256686.5082 | 77413.2844 | 61604.762 | 37.2092
Chemicals | 505675.4621 | 152505.0873 | 202270.1848 | -35.6752 | 505675.4621 | 152505.0873 | 121362.1109 | 37.2092
Oil and Gas | 2177197.7446 | 656614.2854 | 870879.0978 | -35.6752 | 2177197.7446 | 656614.2854 | 522527.4587 | 37.2092
Total |  | 2009557.4234 | 2665311.4237 |  |  | 2009557.4234 | 1599186.8542

## Minimize Vented Steam
Sub-Sector | Percent of Fuel Use By Steam | Calculations
|  | 2008 Emissions (MTCO2e) | Amount of Natural Gas to Produce Steam (MMBTU)
Petroleum | 33.71% | 35006223.7928 | 222643607.529
Food | 63.92% | 1627120.4825 | 19625123.1592
Wood Products | 74.14% | 1193875.2006 | 16700271.1859
Chemicals | 68.18% | 2557335.3031 | 32899732.0831
Oil and Gas | 70% | 10724972.4852 | 141650579.9938
Sub-Sector | Minimize Vented Steam (Category 1) |  |  |  | Minimize Vented Steam (Category 2)
| Feasibility (percent) | Efficiency Increase (percent) | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e) | Feasibility (percent) | Efficiency Increase (percent) | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e)
Petroleum | 4.1% | 2.5% | 228209.6977 | 12095.114 | 4.92% | 1.25% | 136925.8186 | 7257.0684
Food | 6.4% | 2.5% | 31400.1971 | 1664.2104 | 7.68% | 1.25% | 18840.1182 | 998.5263
Wood Products | 6.4% | 2.5% | 26720.4339 | 1416.183 | 7.68% | 1.25% | 16032.2603 | 849.7098
Chemicals | 4.1% | 2.5% | 33722.2254 | 1787.2779 | 4.92% | 1.25% | 20233.3352 | 1072.3668
Oil and Gas | 6.1% | 2.5% | 216017.1345 | 11448.9081 | 7.32% | 1.25% | 129610.2807 | 6869.3449
Total |  |  | 536069.6885 | 28411.6935 |  |  | 321641.8131 | 17047.0161
Interest Rate | Years | Annuity Factor | 2020 Price of Fuel ($/MMBTU) | Carbon Intensity Natural Gas (MTCO2e/MMBTU) | Hours per Year
0.3 | 20 | 0.30159 | 7.6851 | 0.053 | 8760
Sub-Sector | Minimize Vented Steam (Category 1) |  |  |  | Minimize Vented Steam (Category 2)
| Total Capital Cost | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e) | Total Capital Cost | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e)
Petroleum | 876907.174 | 264463.7029 | 1753814.3479 | -123.1366 | 876907.174 | 264463.7029 | 1052288.6088 | -108.5597
Food | 120656.8272 | 36388.5166 | 241313.6544 | -123.1366 | 120656.8272 | 36388.5166 | 144788.1926 | -108.5597
Wood Products | 102674.6033 | 30965.3138 | 205349.2065 | -123.1366 | 102674.6033 | 30965.3138 | 123209.5239 | -108.5597
Chemicals | 129579.3372 | 39079.4286 | 259158.6743 | -123.1366 | 129579.3372 | 39079.4286 | 155495.2046 | -108.5597
Oil and Gas | 830056.6401 | 250334.1963 | 1660113.2803 | -123.1366 | 830056.6401 | 250334.1963 | 996067.9682 | -108.5597
Total |  | 621231.1582 | 4119749.1634 |  |  | 621231.1582 | 2471849.4981

## Insulation Maintenance
Sub-Sector | Percent of Fuel Use By Steam | Calculations
|  | 2008 Emissions (MTCO2e) | Amount of Natural Gas to Produce Steam (MMBTU)
Petroleum | 33.71% | 35006223.7928 | 222643607.529
Food | 63.92% | 1627120.4825 | 19625123.1592
Wood Products | 74.14% | 1193875.2006 | 16700271.1859
Chemicals | 68.18% | 2557335.3031 | 32899732.0831
Oil and Gas | 70% | 10724972.4852 | 141650579.9938
Sub-Sector | Insulation Maintenance (Category 1) |  |  |  | Insulation Maintenance (Category 2)
| Feasibility (percent) | Efficiency Increase (percent) | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e) | Feasibility (percent) | Efficiency Increase (percent) | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e)
Petroleum | 40% | 3.5% | 3117010.5054 | 165201.5568 | 5% | 7.5% | 834913.5282 | 44250.417
Food | 40% | 3.5% | 274751.7242 | 14561.8414 | 5% | 7.5% | 73594.2118 | 3900.4932
Wood Products | 40% | 3.5% | 233803.7966 | 12391.6012 | 5% | 7.5% | 62626.0169 | 3319.1789
Chemicals | 40% | 3.5% | 460596.2492 | 24411.6012 | 5% | 7.5% | 123373.9953 | 6538.8218
Oil and Gas | 40% | 3.5% | 1983108.1199 | 105104.7304 | 5% | 7.5% | 531189.675 | 28153.0528
Total |  |  | 6069270.3953 | 321671.331 |  |  | 1625697.4273 | 86161.9636
Interest Rate | Years | Annuity Factor | 2020 Price of Fuel ($/MMBTU) | Carbon Intensity Natural Gas (MTCO2e/MMBTU) | Hours per Year
0.3 | 20 | 0.30159 | 7.6851 | 0.053 | 8760
Sub-Sector | Insulation Maintenance (Category 1) |  |  |  | Insulation Maintenance (Category 2)
| Total Capital Cost | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e) | Total Capital Cost | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e)
Petroleum | 47909074.8702 | 14448748.6446 | 23954537.4351 | -57.5406 | 19249181.8675 | 5774754.5602 | 6416393.9558 | -14.5002
Food | 4222988.9518 | 1273598.0826 | 2111494.4759 | -57.5406 | 1696736.6324 | 509020.9897 | 565578.8775 | -14.5002
Wood Products | 3593611.1145 | 1083785.9813 | 1796805.5573 | -57.5406 | 1443861.6085 | 433158.4826 | 481287.2028 | -14.5002
Chemicals | 7079456.4689 | 2135071.2227 | 3539728.2344 | -57.5406 | 2844424.4741 | 853327.3422 | 948141.4914 | -14.5002
Oil and Gas | 30480768.4247 | 9192599.9961 | 15240384.2123 | -57.5406 | 12246737.3135 | 3674021.194 | 4082245.7712 | -14.5002
Total |  | 28133803.9272 | 46642949.915 |  |  | 11244282.5688 | 12493647.2987

## Steam Trap Maintenance
Sub-Sector | Percent of Fuel Use By Steam | Calculations
|  | 2008 Emissions (MTCO2e) | Amount of Natural Gas to Produce Steam (MMBTU)
Petroleum | 33.71% | 35006223.7928 | 222643607.529
Food | 63.92% | 1627120.4825 | 19625123.1592
Wood Products | 74.14% | 1193875.2006 | 16700271.1859
Chemicals | 68.18% | 2557335.3031 | 32899732.0831
Oil and Gas | 70% | 10724972.4852 | 141650579.9938
Sub-Sector | Steam Trap Maintenance (Category 1) |  |  |  | Steam Trap Maintenance (Category 2)
| Feasibility (percent) | Efficiency Increase (percent) | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e) | Feasibility (percent) | Efficiency Increase (percent) | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e)
Petroleum | 50% | 3% | 3339654.1129 | 177001.668 | 30% | 5% | 3339654.1129 | 177001.668
Food | 50% | 3% | 294376.8474 | 15601.9729 | 30% | 5% | 294376.8474 | 15601.9729
Wood Products | 50% | 3% | 250504.0678 | 13276.7156 | 30% | 5% | 250504.0678 | 13276.7156
Chemicals | 50% | 3% | 493495.9812 | 26155.287 | 30% | 5% | 493495.9812 | 26155.287
Oil and Gas | 50% | 3% | 2124758.6999 | 112612.2111 | 30% | 5% | 2124758.6999 | 112612.2111
Total |  |  | 6502789.7093 | 344647.8546 |  |  | 6502789.7093 | 344647.8546
Interest Rate | Years | Annuity Factor | 2020 Price of Fuel ($/MMBTU) | Carbon Intensity Natural Gas (MTCO2e/MMBTU) | Hours per Year
0.3 | 20 | 0.30159 | 7.6851 | 0.053 | 8760
Sub-Sector | Steam Trap Maintenance (Category 1) |  |  |  | Steam Trap Maintenance (Category 2)
| Total Capital Cost | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e) | Total Capital Cost1 | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e)
Petroleum | 25665575.8233 | 7740401.0596 | 25665575.8233 | -101.2712 | 38498363.735 | 11549509.1205 | 25665575.8233 | -79.751
Food | 2262315.5099 | 682284.6871 | 2262315.5099 | -101.2712 | 3393473.2648 | 1018041.9794 | 2262315.5099 | -79.751
Wood Products | 1925148.8114 | 580599.6328 | 1925148.8114 | -101.2712 | 2887723.217 | 866316.9651 | 1925148.8114 | -79.751
Chemicals | 3792565.9655 | 1143788.155 | 3792565.9655 | -101.2712 | 5688848.9482 | 1706654.6845 | 3792565.9655 | -79.751
Oil and Gas | 16328983.0847 | 4924607.1407 | 16328983.0847 | -101.2712 | 24493474.627 | 7348042.3881 | 16328983.0847 | -79.751
Total |  | 15071680.6753 | 49974589.1947 |  |  | 22488565.1376 | 49974589.1947
1 For Category 2, staff assumed a 50 percent greater cost than Category 1

## Steam Leak Maintenance
Sub-Sector | Percent of Fuel Use By Steam | Calculations
|  | 2008 Emissions (MTCO2e) | Amount of Natural Gas to Produce Steam (MMBTU)
Petroleum | 33.71% | 35006223.7928 | 222643607.529
Food | 63.92% | 1627120.4825 | 19625123.1592
Wood Products | 74.14% | 1193875.2006 | 16700271.1859
Chemicals | 68.18% | 2557335.3031 | 32899732.0831
Oil and Gas | 70% | 10724972.4852 | 141650579.9938
Sub-Sector | Steam Leak Maintenance (Category 1) |  |  |  | Steam Leak Maintenance (Category 2)
| Feasibility (percent) | Efficiency Increase (percent) | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e) | Feasibility (percent) | Efficiency Increase (percent) | Total Fuel Reduction (MMBTU) | GHG Reduction (MTCO2e)
Petroleum | 20% | 2.5% | 1113218.0376 | 59000.556 | 30% | 1% | 667930.8226 | 35400.3336
Food | 20% | 2.5% | 98125.6158 | 5200.6576 | 30% | 1% | 58875.3695 | 3120.3946
Wood Products | 20% | 2.5% | 83501.3559 | 4425.5719 | 30% | 1% | 50100.8136 | 2655.3431
Chemicals | 20% | 2.5% | 164498.6604 | 8718.429 | 30% | 1% | 98699.1962 | 5231.0574
Oil and Gas | 20% | 2.5% | 708252.9 | 37537.4037 | 30% | 1% | 424951.74 | 22522.4422
Total |  |  | 2167596.5698 | 114882.6182 |  |  | 1300557.9419 | 68929.5709
Interest Rate | Years | Annuity Factor | 2020 Price of Fuel ($/MMBTU) | Carbon Intensity Natural Gas (MTCO2e/MMBTU) | Hours per Year
0.3 | 20 | 0.30159 | 7.6851 | 0.053 | 8760
Sub-Sector | Steam Leak Maintenance (Category 1) |  |  |  | Steam Leak Maintenance (Category 2)
| Total Capital Cost | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e) | Total Capital Cost1 | Total Annual Capital Cost | Total Annual Savings | Abatement Cost ($/MTCO2e)
Petroleum | 12832787.9117 | 3870200.5298 | 8555191.9411 | -79.4059 | 19249181.8675 | 5805300.7947 | 5133115.1647 | 18.9881
Food | 1131157.7549 | 341142.3435 | 754105.17 | -79.4059 | 1696736.6324 | 511713.5153 | 452463.102 | 18.9881
Wood Products | 962574.4057 | 290299.8164 | 641716.2705 | -79.4059 | 1443861.6085 | 435449.7246 | 385029.7623 | 18.9881
Chemicals | 1896282.9827 | 571894.0775 | 1264188.6552 | -79.4059 | 2844424.4741 | 857841.1162 | 758513.1931 | 18.9881
Oil and Gas | 8164491.5423 | 2462303.5704 | 5442994.3616 | -79.4059 | 12246737.3135 | 3693455.3556 | 3265796.6169 | 18.9881
Total |  | 7535840.3376 | 16658196.3982 |  |  | 11303760.5065 | 9994917.8389
1 For Category 2, staff assumed a 50 percent greater cost than Category 1