Application No.:  363819

Equipment Category - Absorption Chiller

| 1. GENERAL INFORMATION |  | DATE: 5/5/1999 |
| --- | --- | --- |
| a. manufacturer: Trane |
| b. type: Direct Fired | c. model: ABDA 0440 |
| d. style: |
| e. applicable aqmd regulation xi rules: Rule 1146 |
| f. cost: $ ( ) source of cost data: |
| g. operating schedule: 10 hrs/day 5 days/wk 52 wks/yr |

| 2. EQUIPMENT INFORMATION |  | App. No.: 363819 |
| --- | --- | --- |
| A. FUNCTION: Provide cooling to buildings during peak demand periods |
| B. maximum Heat Input: 5.05 MMBtu/hr | C. maximum throughput: 464 tons cooling |
| D. burner information: no.: 1 type: Weishaupt Low NOx Burner |
| e. primary fuel: Natural Gas | f. other fuel: |
| g. operating conditions: |

| 3. COMPANY INFORMATION |  | App. No.: 363819 |
| --- | --- | --- |
| A. NAME: College of the Desert |
| B. ADDRESS: 43-500 Monterey Ave. CITY: Palm Desert STATE: CA ZIP: 92260 |
| C. CONTACT PERSON: Steve Renew | D. PHONE NO.: (760) 773-2551 |

| 4. PERMIT INFORMATION |  | App. No.: 363819 |
| --- | --- | --- |
| A. AGENCY: `SCAQMD' | B. application type: |
| C. AGENCY CONTACT PERSON: Maria Vibal | D. PHONE NO.: (909) 396 - 2422 |
| E. PERMIT TO CONSTRUCT INFORMATION: P/C NO.: ISSUANCE DATE: check if no p/c |
| F. START-UP DATE: June 15, 1999 |
| G. PERMIT TO OPERATE INFORMATION: P/O NO.: F25619 ISSUANCE DATE: 3/16/2000 |

| 5. EMISSION INFORMATION |  | App. No.: 363819 |
| --- | --- | --- |
| A. PERMIT |
| A1. PERMIT LIMIT: 20 ppmv NOx @ 3%O2 and 50 ppmv CO @ 3% O2. |
| A2. bact/lAer DETERMINATION: Natural Gas, Low NOx Burner, and Flue Gas Recirculation |
| B. CONTROL TECHNOLOGY |
| B1. MANUFACTURER/SUPPLIER: Weishaupt Corporation |
| B2. TYPE: low-NOx burner and flue gas recirculation |
| B3. DESCRIPTION: |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: ISSUANCE DATE: P/O NO.: F25619 ISSUANCE DATE: 3/16/2000 |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: HP |
| B6. WARRANTY: |
| B7. PRIMARY POLLUTANTS: NOx, CO, PM10, VOC, SOx |
| B8. SECONDARY POLLUTANTS: none |
| B9. SPACE REQUIREMENT: |
| B10. LIMITATIONS: |
| B11. LOCATION OF PRIOR DEMONSTRATION & AGENCY: FACILITY: Marriott's Desert Springs Resort & Spa CONTACT PERSON: Scott Carlson PHONE NO.: (760) 341-1761 AGENCY: SCAQMD ADDRESS: Diamond Bar, CA CONTACT PERSON: Maria Vibal PHONE NO.: (909) 396-2422 |
| B12. OPERATING HISTORY: |
| B13. SOURCE TEST/PERFORMANCE DATA ANALYSIS: DATE OF SOURCE TEST: 2/24/2000 CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICEINCY: PERFORMANCE DATA: see below NOx emissions: 14.65 ppmv @ 3% O2 at 20% firing rate, 16.81 ppmv @ 3% O2 at 50% firing rate, and 19.10 ppmv @ 3% O2 at 100% firing rate CO emissions: < 1ppmv at each load. |
| B14. SOURCE TEST CONDITIONS/PERFORMANCE DATA: |
| C. COST |
| C1. CONTROL EQUIPMENT COST: check if installation cost is included in capital cost CAPITAL: $ INSTALLATION: $ ( ) SOURCE OF COST DATA: |
| C2. ANNUAL OPERATIONAL/MAINTENANCE COST: $ ( ) SOURCE OF COST DATA: |
| D. DEMONSTRATION OF COMPLIANCE |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: DATE: |
| D2. COMPLIANCE DEMONSTRATION: |
| D3. VARIANCE: NO. OF VARIANCES: DATES: CAUSES: |
| D4. VIOLATION: NO. OF VIOLATIONS: DATES: CAUSES: |
| D5. FREQUENCY OF MAINTENANCE: The burner is equipped with a control system that automatically regulates combustion air, fuel, and recirculated flue gas as the chiller load varies. This automatic control system shall be tuned at least twice a year according to the manufacturer's specifications. |

| 6. COMMENTS |  | App. No.: 363819 |
| --- | --- | --- |
| Direct-fired absorption chillers are designed to provide comfort cooling or to supply chilled water. Direct-fired absorbtion chillers use water as refrigerant and lithium bromide as absorbent. The main components of a direct absorption chiller are 1) evaporator/absorber, 2) direct-fired generator, and 3) condensor. Prior BACT determinations: 1) A 7.6 mmbtu/hr natural gas fired absorption chiller with Coen Micro NOx-10 achieving 20 ppmv NOx @ 3% O2, permit issued on 11/12/99 by San Joaquin Valley Unified APCD; 2) Two 5.0 mmbtu/hr McQuay, Model No. TSA-DC51W-ROZ, abosrption chillers with Weishaupt low NOx burners achieving 20 ppmv NOx @ 3% O2 and 50 ppmv CO @ 3% O2, permit issued on 11/04/99 by SCAQMD. |