Application No.:  394164

Equipment Category - Gas Turbine

| 1. GENERAL INFORMATION |  | DATE: 1/30/2004 |
| --- | --- | --- |
| a. manufacturer: Alstom |
| b. type: Combined Cycle | c. model: GTX100 |
| d. style: With duct burner |
| e. applicable aqmd rules: 212, 218, 401, 402, 403, 407, 431.1, 475, Reg. XIII, 1401, Reg. XX, Reg. XXX, CEQA, 40CFR Part 60 subpart GG, 40CFR Part 63 NESHAPS, 40CFR Part 64, 40CFR Part 72 |
| f. cost: $ () source of cost data: |
| g. operating schedule: 24 hrs/day 7 days/wk 52 wks/yr |

| 2. EQUIPMENT INFORMATION |  | App. No.: 394164-165 |
| --- | --- | --- |
| A. FUNCTION: Power Generation |
| B. maximum Heat Input: 525 mmbtu/hr (turbine) and 73 mmbtu/hr (duct burner) | C. maximum throughput: 43 MW gas turbine, 55 MW steam turbine |
| D. burner information: no.: type: Dry Low-NOx |
| e. primary fuel: Natural Gas | f. other fuel: |
| g. operating conditions: Baseload, load following |

| 3. COMPANY INFORMATION |  | App. No.: 394164-165 |
| --- | --- | --- |
| A. NAME: Vernon City Light & Power | B. SIC CODE: 4911 |
| C. ADDRESS: 2715 E 50th Street CITY: Vernon STATE: CA ZIP: 90058 |
| D. CONTACT PERSON: Mr. Carlos Fandino | E. PHONE NO.: (323) 583 - 8811x573 |

| 4. PERMIT INFORMATION |  | App. No.: 394164-165 |
| --- | --- | --- |
| A. AGENCY: SCAQMD | B. application type: |
| C. AGENCY CONTACT PERSON: Chandrashekhar S. Bhatt | D. PHONE NO.: (909) 396 - 2653 |
| E. PERMIT TO CONSTRUCT/OPERATE INFORMATION: P/C NO.: 394164 ISSUANCE DATE: 5/27/2003 check if no p/c P/O NO.: ISSUANCE DATE: |
| F. START-UP DATE: Fall 2004 (est.) |

| 5. EMISSION INFORMATION |  | App. No.: 394164-165 |
| --- | --- | --- |
| A. PERMIT |
| A1. PERMIT LIMIT: ppmvd @15% O2 : NOx 2.0 (1-hr), CO 2.0 (3-hr), VOC 2.0 (1-hr), NH3 5.0 (1-hr). PM 0.01 gr/scf and 11 lb/hr. Monthly mass limits on CO, PM10, VOC and SOx. |
| A2. bact/lAer DETERMINATION: Above limits on NOx, VOC and NH3 were believed to represent BACT for a combined cycle gas turbine. The CO limit is more stringent than prior BACT. |
| a3. BASIS OF THE BACT/LAER DETERMINATION: Prior BACT determination was based on CARB's Guidance Document for Power Plant Sitings, dated September 1999 and the ANP Blackstone combined-cycle power plant in Massachusetts (AQMD Public Notice 1/16/2003). The more stringent limit for CO was proposed by the applicant to reduce the offset requirements. Magnolia Power Project (A/N 386305) has similar concentration limits of NOx, CO, VOC and NH3 except for differences in averaging times (3-hr for NOx and 1-hr for VOC). |
| B. CONTROL TECHNOLOGY |
| B1. MANUFACTURER/SUPPLIER: Mitsubishi/Cormetec (SCR system), Emerachem (oxidation catalyst) |
| B2. TYPE: SCR system and oxidation catalyst |
| B3. DESCRIPTION: Low temperature SCR catalyst with aqueous ammonia (19% by weight) |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: 394166 ISSUANCE DATE: 5/27/2003 P/O NO.: ISSUANCE DATE: |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: |
| B6. WARRANTY: |
| B7. PRIMARY POLLUTANTS: NOx, CO, PM,VOC, SOx |
| B8. SECONDARY POLLUTANTS: NH3 |
| B9. SPACE REQUIREMENT: SCR catalyst total space requirement = 1,816 cu. ft; SCR catalyst volume = 537.1 cu. ft.; CO catalyst total space requirement = 638 cu. ft; CO catalyst volume: 63 cu. ft. There are 2 such units at MGS Power Plant. |
| B10. LIMITATIONS: | B11. UNUSED |
| B12. OPERATING HISTORY: |
| B13. UNUSED | B14. UNUSED |
| C. CONTROL EQUIPMENT COSTS |
| C1. CAPITAL COST: check if installation cost is included in EQUIPMENT cost EQUIPMENT: $ INSTALLATION: $ () SOURCE OF COST DATA: |
| C2. ANNUAL OPERATING COST: $ () SOURCE OF COST DATA: |
| D. DEMONSTRATION OF COMPLIANCE |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: DATE: |
| D2. COMPLIANCE DEMONSTRATION: Source test within 180 days after startup. NOx/CO CEMS. |
| D3. VARIANCE: NO. OF VARIANCES: DATES: CAUSES: |
| D4. VIOLATION: NO. OF VIOLATIONS: DATES: CAUSES: |
| D5. MAINTENANCE REQUIREMENTS: | D6. UNUSED |
| D7. SOURCE TEST/PERFORMANCE DATA RESULTS AND ANALYSIS: DATE OF SOURCE TEST: CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICIENCY: SOURCE TEST/PERFORMANCE DATA: OPERATING CONDITIONS: TEST METHODS: |

| 6. COMMENTS |  | App. No.: 394164-165 |
| --- | --- | --- |
| There is also an identical power production unit and SCR system (A/N's 394165 and 394167). |