Application No.:  371784

Equipment Category – Process Heater - Non-Refinery

| 1. GENERAL INFORMATION |  | DATE: 11/7/2002 |
| --- | --- | --- |
| a. manufacturer: American Hydrotherm |
| b. type: Forced Circulation | c. model: 1200-4D-90 |
| d. style: Horizontal Double-Pipe Coil |
| e. applicable aqmd regulation xi rules: 1146 |
| f. cost: $ () source of cost data: |
| g. operating schedule: 24 hrs/day 7 days/wk 52 wks/yr |

| 2. EQUIPMENT INFORMATION |  | App. No.: 371784 |
| --- | --- | --- |
| A. FUNCTION: Heats recirculating oil used in laminating presses. |
| B. maximum Heat Input: 19 MMBtu/hr | C. maximum throughput: |
| D. burner information: no.: 1 type: Ultra Low-NOx |
| e. primary fuel: Natural Gas | f. other fuel: None |
| g. operating conditions: Average firing rate = 60% |

| 3. COMPANY INFORMATION |  | App. No.: 371784 |
| --- | --- | --- |
| A. NAME: NELCO Products, Inc. | B. SIC CODE: 3672 |
| C. ADDRESS: 1411 E. Orangethorpe Ave. CITY: Fullerton STATE: CA ZIP: 92831 |
| D. CONTACT PERSON: Jennifer Sanchez | E. PHONE NO.: 714-879-4293 |

| 4. PERMIT INFORMATION |  | App. No.: 371784 |
| --- | --- | --- |
| A. AGENCY: SCAQMD | B. application type: |
| C. AGENCY CONTACT PERSON: Rick Lee | D. PHONE NO.: 909-396-2629 |
| E. PERMIT TO CONSTRUCT/OPERATE INFORMATION: P/C NO.: 371784 ISSUANCE DATE: 8/4/2000 check if no p/c P/O NO.: 371784 ISSUANCE DATE: 12/5/2001 |
| F. START-UP DATE: 2/1/01 (Approx.) |

| 5. EMISSION INFORMATION |  | App. No.: 371784 |
| --- | --- | --- |
| A. PERMIT |
| A1. PERMIT LIMIT: 12 ppmd NOx (3% O2), 50 ppmd CO (3% O2), Natural Gas Only |
| A2. bact/lAer DETERMINATION: Same as 5-A1 |
| a3. BASIS OF THE BACT/LAER DETERMINATION: Suggested by Applicant |
| B. CONTROL TECHNOLOGY |
| B1. MANUFACTURER/SUPPLIER: Alzeta Corp. |
| B2. TYPE: Ultra Low-NOx Burner (ULNB) |
| B3. DESCRIPTION: Model CSB-22-250-30/15 pre-mixed, porous-surface burner. Dimensions: 22" D x 45" L. Turndown: 4:1. Operates at 70% excess air at full load (5090 scfm). Pressure drop at full load is 4-6" w.g.. 25 hp blower required. |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: ISSUANCE DATE: P/O NO.: ISSUANCE DATE: |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: |
| B6. WARRANTY: 12 ppm NOx and 50 ppm CO were guaranteed by American Hydrotherm. 9 ppm NOx and 50 ppm CO were guaranteed by Alzeta. All guaranteed ppm were dry basis, corrected to 3% O2. |
| B7. PRIMARY POLLUTANTS: NOx, CO, NMHC, PM, SOx |
| B8. SECONDARY POLLUTANTS: None |
| B9. SPACE REQUIREMENT: |
| B10. LIMITATIONS: | B11. UNUSED |
| B12. OPERATING HISTORY: Has been in regular use since startup. Facility contact person believes the heater may have started up before the expected Feb 2001 date. |
| B13. UNUSED | B14. UNUSED |
| C. CONTROL EQUIPMENT COSTS |
| C1. CAPITAL COST: check if installation cost is included in EQUIPMENT cost EQUIPMENT: $ INSTALLATION: $ () SOURCE OF COST DATA: |
| C2. ANNUAL OPERATING COST: $ () SOURCE OF COST DATA: |
| D. DEMONSTRATION OF COMPLIANCE |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: Lily Henry DATE: 10/23/2001 |
| D2. COMPLIANCE DEMONSTRATION: |
| D3. VARIANCE: NO. OF VARIANCES: None DATES: CAUSES: |
| D4. VIOLATION: NO. OF VIOLATIONS: None DATES: CAUSES: |
| D5. MAINTENANCE REQUIREMENTS: | D6. UNUSED |
| D7. SOURCE TEST/PERFORMANCE DATA RESULTS AND ANALYSIS: DATE OF SOURCE TEST: 3/27/2001 CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICEINCY: Test Condition Low Fire High Fire Heat Input, MMBtu/hr 5.1 15.3 O2, % (dry) 8.8 9.2 NOx, ppm (dry, 3% O2) 4.5 3.3 CO, ppm (dry, 3% O2) <1 <1 Source test accepted by AQMD Monitoring & Source Test Engineering group. SOURCE TEST/PERFORMANCE DATA: OPERATING CONDITIONS: High and low firing rates TEST METHODS: AQMD Method 100.1 |

| 6. COMMENTS |  | App. No.: 371784 |
| --- | --- | --- |
| American Hydrotherm is no longer in business. However, Alzeta still offers this burner for horizontal double-coil heaters (e.g., American Heater Co.). |