## Blackstart Emissions
DWP HARBOR AND VALLEY STATIONS
BLACK START GENERATOR SET
CARB Air Toxic Emission Factors
Device ID Number: | Black Start Diesel Generator Set
Process Description:
No. of Devices: | 1
Process Equipment Description: | 565 kW Diesel Generator Set
Fuel Type: | No. 2. Diesel Fuel
Process Units: | 1000 gal
Control Equipment: | None
Control Type:
Estimation Method: | Emission Factors
Yearly Emis. Est. Equation: | Fy x EF
Max Hourly Emis. Est. Equation: | Fm x EF
Parameter Symbols/Names |  |  | Values
Fy = Total Yearly Amount of Fuel Burned |  |  | NA | 1000gal
Fm = Maximum Hourly Amount of Fuel Burned |  |  | 0.022 | 1000gal
EF = Emission Factor |  |  | See Below
Process Operation Schedule |  |  | 0.5 | hours/day
|  |  | 1 | days/week
|  |  | 12 | week/yr
Emittent | Emittent ID | Emission | Max | Operating | Annual(1)
Species Name | (CAS Number) | Factor | Emissions | Emissions | Oil-fired
|  | lbs/1000gal | (lbs) | (grams/sec) | (lbs/yr)
NOx | Criteria | 306.01 | 6.73 | 0.85 | 80.76
CO | Criteria | 132.05 | 2.91 | 0.37 | 34.92
VOC | Criteria | 48.65 | 1.07 | 0.13 | 12.84
PM | Criteria | 43.09 | 0.95 | 0.12 | 11.4
SO2 | Criteria | 7.09 | 0.16 | 0.02 | 1.92
1,3-Butadiene | 106990 | 0.00541 | 0.00011902 | 1.501e-05 | 0.0014282
Acrolein | 107028 | 0.013 | 0.000286 | 3.6068e-05 | 0.003432
Benz(a)anthracene (PAH) | 56553 | 0.000234 | 5.148e-06 | 6.4922e-07 | 6.1776e-05
Benzene | 71432 | 0.122 | 0.002684 | 0.00033848 | 0.032208
Benzo(a)pyrene (PAH) | 50328 | 1.81e-05 | 3.982e-07 | 5.0217e-08 | 4.7784e-06
Benzo(b)fluoranthene (PAH) | 205992 | 8.66e-05 | 1.9052e-06 | 2.4027e-07 | 2.2862e-05
Benzo(k)fluoranthene (PAH) | 207089 | 3.28e-05 | 7.216e-07 | 9.1002e-08 | 8.6592e-06
Chrysene (PAH) | 218019 | 5.3e-05 | 1.166e-06 | 1.4705e-07 | 1.3992e-05
Dibenz(a,h)anthracene (PAH) | 53703 | 5.5e-05 | 1.21e-06 | 1.5259e-07 | 1.452e-05
Formaldehyde | 50000 | 0.116 | 0.002552 | 0.00032184 | 0.030624
Indeno(1,2,3-cd)pyrene (PAH) | 193395 | 4.63e-05 | 1.0186e-06 | 1.2846e-07 | 1.2223e-05
Naphthalene (PAH) | 91203 | 0.0544 | 0.0011968 | 0.00015093 | 0.014362
Propylene | 115071 | 0.358 | 0.007876 | 0.00099325 | 0.094512
Toluene | 10883 | 0.055 | 0.00121 | 0.00015259 | 0.01452
Xylene, Total | 1330207 | 0.0359 | 0.0007898 | 9.9603e-05 | 0.0094776
|  |  | 0.016725 |  | 0.2007

## EF Criteria
DEVELOPMENT OF CRITERIA POLLUTANT EMISSON FACTORS
FOR THE BLACK START GENERATOR SET AT THE HARBOR AND VALLEY PLANTS
(No. 2 Diesel Fuel Use by the Generator Set)
1. The Black Start Generator Set is a 565 kW diesel unit. It provides the power to start one combustion turbine(1).
2. The diesel fuel will have a HHV of 139,000 Btu/gal (2) and an estimated LHV of 126,000 Btu/gal.
3. The efficiency is 40% and the generator will be tested monthly. (3)
4. The operating time for the Black Start Generator Set should not exceed 30 minutes. (3)
5. The maxumum fuel use is 44.5 gallons per hour and the stack gas flow rate is 5014 ACFM.(4)
6. The stack temperature is 906 oF. (4)
7. The NOx emission rate is 6.9 grams/bhp-hr. (5)
Horsepower = | 896
Maximum Firing Rate = |  | 44.5 | gal/hr
| Size |  | HHV (2) | MFR
| (kW) |  | (Btu/gal) | (Btu/hr)
| 565 |  | 139000 | 6185500
Fuel Consumption Rate for Black Start Test and CT Start-up = |  |  |  | 0.022 | Mgal
Calculate NOx Emissions
NOx = 6.9 grams/bhp-hr x hp/(454 x fuel)
| HP | Fuel | NOx | NOx
|  | (gal/hr) | (grams/bhp) | (lbs/Mgal)
| 896 | 44.5 | 6.9 | 306.01
Pollutant |  | Fuel | EL (6) | EF
|  | (Mgal/hr) | (lb/MMBtu) | (lb/Mgal)
CO |  | 0.022 | 0.95 | 132.05
VOC (CH4) |  | 0.022 | 0.35 | 48.65
PM10 |  | 0.022 | 0.31 | 43.09
SO2 (6)(7) |  | 0.022 | 0.051 | 7.09
Emission Factor for Sulfur Dioxide (SO2) (7)
| Pollutant | Emission | Sulfur | Emission
|  | Factor | Content | Factor
|  | (lbs/MMBtu) | (wt %) (7) | (lbs/MMBtu)
| SO2 | 1.01S | 0.05 | 0.051
Stack Gas Flow | Stack Inside Diameter(3) | Stack Exit Velocity | Stack Exit Velocity | Stack Inside Diameter | Stack Height (3) | Stack Height
(ACFM) | (FT) | (FT/SEC) | (M/SEC) | (M) | (FT) | (M)
5014 | 0.667 | 239.16 | 72.9 | 0.2 | 110 | 33.53
ALTERNATIVE STACK GAS DISCHARGE THROUGH CT STACK - NONE OPERATION OF CT
STACK TEMPERATURE 906 oF
Stack Gas Flow | Stack Inside Diameter(3) |  | Stack Exit Velocity | Stack Inside Diameter | Stack Height (3) | Stack Height
(ACFM) | (FT) | (FT/SEC) | (M/SEC) | (M) | (FT) | (M)
5014 | 10 | 1.06 | 0.32 | 3.05 | 110 | 33.53
ALTERNATIVE STACK GAS DISCHARGE THROUGH CT STACK - OPERATION OF CT
Stack Temperature 824 oF at Valley and 841 oF at Harbor
Valley Stack Gas Flow | Stack Inside Diameter(3) | Stack Exit Velocity | Stack Exit Velocity | Stack Inside Diameter | Stack Height (3) | Stack Height
(ACFM) | (FT) | (FT/SEC) | (M/SEC) | (M) | (FT) | (M)
557813 | 10 | 118.37 | 36.08 | 3.05 | 110 | 33.53
Harbor Stack Gas Flow | Stack Inside Diameter(3) | Stack Exit Velocity | Stack Exit Velocity | Stack Inside Diameter | Stack Height (3) | Stack Height
(ACFM) | (FT) | (FT/SEC) | (M/SEC) | (M) | (FT) | (M)
543966 | 10 | 115.43 | 35.18 | 3.05 | 110 | 33.53
(1) Specification provided by LA DWP from Request for Proposal dated September 25, 2000 and
S & S Energy Products' Specifications sheet.
(2) AP-42, Section 3.3 Gasoline and Diesel Industrial Engines.
(3) Information provided by LA DWP in an e-mail to Krishna Nand from R. Radmaker on 10-27-00 and 11-01-00.
(4) Information provided by LA DWP fax to Krishna Nand from Bruce Moore (Caterpillar Data)
(5) Information from Matt Lambert of Caterpillar provided on 11-02-00.
(6) Emission Factors in lb/MMBtu is from AP-42, Table 3.3-1. SO2 factor from this table not used.
(7) Emission Factor from AP-42, Table 3.1-2a. AP-42, Section 3.3 does not address sulfur content.
(8) Maximum value for No. 2 Diesel Oil.

## Air Toxics EF
CARB AIR TOXICS EMISSION FACTORS
BLACK START GENERATOR SET
DIESEL RECIPROCATING ENGINE
Air Toxics Emission factors are from California Air Resources Board's latest air toxics data.
Lean Burn emission factors selected.
Substance | Air Toxic | CAS No. | Rule 1401 | Mean Emission
Category |  |  | Listed Air | Factor
|  |  | Toxic (Y/N) | (lbs/MGAL)
VOC | 1,3-Butadiene | 106990 | Y | 0.00541
PAH | Acenaphthene (PAH) | 83329 | N | 0.00314
PAH | Acenaphthylene (PAH) | 208968 | N | 0.00407
VOC | Acrolein | 107028 | Y | 0.013
PAH | Anthracene (PAH) | 120127 | N | 0.000848
Metal | Arsenic | 7440382 | Y | 0
SVOC | Benzaldehyde | 100527 | N | 0.0126
PAH | Benz(a)anthracene (PAH) | 56553 | Y | 0.000234
VOC | Benzene | 71432 | Y | 0.122
PAH | Benzo(a)pyrene (PAH) | 50328 | Y | 1.81e-05
PAH | Benzo(b)fluoranthene (PAH) | 205992 | Y | 8.66e-05
PAH | Benzo(b+k)fluoranthene (PAH) | --- | N | 1.44e-06
PAH | Benzo(g,h,i)perylene (PAH) | 191242 | N | 4.94e-05
PAH | Benzo(k)fluoranthene (PAH) | 207089 | Y | 3.28e-05
Metal | Beryllium | 7440417 | Y | 0
Metal | Cadmium | 7440439 | Y | 0
PAH | Chrysene (PAH) | 218019 | Y | 5.3e-05
Metal | Chromium (Hex) | 18540299 | Y | 0
Metal | Chromium (total) | 7440473 | Y | 0
Metal | Copper | 7440508 | Y | 0
PAH | Dibenz(a,h)anthracene (PAH) | 53703 | Y | 5.5e-05
Diox/Furan | Dioxin: 4D Total | 41903575 | Y | 0
Diox/Furan | Dioxin: 5D Total | 36088229 | Y | 0
Diox/Furan | Dioxin: 6D Total | 34465468 | Y | 0
Diox/Furan | Dioxin: 7D Total | 37871004 | Y | 0
Diox/Furan | Dioxin: 8D | 3268879 | Y | 0
PAH | Fluoranthene (PAH) | 206440 | N | 0.00133
PAH | Fluorene (PAH) | 86737 | N | 0.00552
VOC | Formaldehyde | 50000 | Y | 0.116
Diox/Furan | Furan: 4F Total | 55722275 | Y | 0
Diox/Furan | Furan: 5F Total | 30402154 | Y | 0
Diox/Furan | Furan: 6F Total | 55684941 | Y | 0
Diox/Furan | Furan: 7F Total | 38998753 | Y | 0
Diox/Furan | Furan: 8F | 39001020 | Y | 0
Halogens | HCL | 7647010 | Y | 0
PAH | Indeno(1,2,3-cd)pyrene (PAH) | 193395 | Y | 4.63e-05
Metals | Lead | 7439921 | Y | 0
Metals | Managanese | 7439965 | Y | 0
Metals | Mercury | 7439976 | Y | 0
PAH | Naphthalene (PAH) | 91203 | Y | 0.0544
Metals | Nickel | 7440020 | Y | 0
PAH | Phenanthrene PAH) | 85018 | N | 0.00947
VOC | Propylene | 115071 | Y | 0.358
PAH | Pyrene (PAH) | 129000 | N | 0.000902
Metals | Selenium | 7782492 | Y | 0
VOC | Toluene | 10883 | Y | 0.055
VOC | Xylene, Total | 1330207 | Y | 0.0359
Metals | Zinc | 7440666 | Y | 0