## Emission Rates
DWP HARBOR STATION
No. 2 Diesel Fuel Readiness Test -- No SCR or CO Catalyst
CARB Toxic Factors
Device ID Number: | Combustion Turbines 1 through 5
Process Description:
No. of Devices: | 5 (Note: Emissions are estimated for one combustion turbine)
Process Equipment Description: | GE LM6000, Sprint 47.3 MW
Fuel Type: | Diesel
Process Units: | 1000 gal
Control Equipment: | Water Injection No Control first 5 minutes.
Control Type:
Estimation Method: | EF
Yearly Emis. Est. Equation: | Fy x EF
Max Hourly Emis. Est. Equation: | Fm x EF
Parameter Symbols/Names |  |  |  | Values
Fy = Total Yearly Amount of Fuel Burned |  |  |  | NA | 1000gal
Fm = Fuel Burned During First 5 Minutes |  |  |  | 0.076 | 1000gal
Fr = Fuel Burned during Remainder of Test |  |  |  | 0.778 | 1000gal
EF =Emission Factors |  |  |  | See Below
Process Operation Schedule |  |  |  | 0.5 | hours/day
|  |  |  | 1 | days/week
|  |  |  | 12 | week/yr
Emittent | Emittent ID | Uncontrolled | Controlled | Total | Total | Annual(1)
Species Name | (CAS Number) | Emission | Emission | Test | Test Hrly | Test
|  | Factor | Factor | Emissions | Emissions | Oil-fired
|  | (lbs/1000gal) | (lbs/1000gal) | (lbs/test) | (grams/sec) | (lbs/yr)
NOx | Criteria | 88.54 | 23.07 | 24.68 | 3.11 | 296.16
CO | Criteria | 1.72 | 14.32 | 11.27 | 1.42 | 135.24
VOC | Criteria | 1.12 | 1.12 | 0.96 | 0.12 | 11.52
PM | Criteria | 1.67 | 1.67 | 1.43 | 0.18 | 17.16
SO2 | Criteria | 7.09 | 7.09 | 6.05 | 0.76 | 72.6
Arsenic | 7440382 | 0.000202 | 0.000202 | 0.00017251 | 2.1755e-05 | 0.0020701
Benz(a)anthracene (PAH) | 56553 | 8.53e-05 | 8.53e-05 | 7.2846e-05 | 9.1867e-06 | 0.00087415
Benzene | 71432 | 0.0113 | 0.0113 | 0.0096502 | 0.001217 | 0.1158
Benzo(a)pyrene (PAH) | 50328 | 8.33e-05 | 8.33e-05 | 7.1138e-05 | 8.9713e-06 | 0.00085366
Benzo(b)fluoranthene (PAH) | 205992 | 0.000132 | 0.000132 | 0.00011273 | 1.4216e-05 | 0.0013527
Benzo(k)fluoranthene (PAH) | 207089 | 0.00013 | 0.00013 | 0.00011102 | 1.4001e-05 | 0.0013322
Beryllium | 7440417 | 5.43e-05 | 5.43e-05 | 4.6372e-05 | 5.848e-06 | 0.00055647
Cadmium | 7440439 | 0.000325 | 0.000325 | 0.00027755 | 3.5002e-05 | 0.0033306
Chrysene (PAH) | 218019 | 0.000103 | 0.000103 | 8.7962e-05 | 1.1093e-05 | 0.0010555
Chromium (Hex) | 18540299 | 1.08e-05 | 1.08e-05 | 9.2232e-06 | 1.1631e-06 | 0.00011068
Chromium (total) | 7440473 | 0.000424 | 0.000424 | 0.0003621 | 4.5664e-05 | 0.0043452
Copper | 7440508 | 0.000998 | 0.000998 | 0.00085229 | 0.00010748 | 0.010228
Dibenz(a,h)anthracene (PAH) | 53703 | 8.25e-05 | 8.25e-05 | 7.0455e-05 | 8.8852e-06 | 0.00084546
Dioxin: 4D Total | 41903575 | 3.74e-09 | 3.74e-09 | 3.194e-09 | 4.0279e-10 | 3.8328e-08
Dioxin: 5D Total | 36088229 | 7.15e-09 | 7.15e-09 | 6.1061e-09 | 7.7005e-10 | 7.3273e-08
Dioxin: 6D Total | 34465468 | 9e-09 | 9e-09 | 7.686e-09 | 9.6929e-10 | 9.2232e-08
Dioxin: 7D Total | 37871004 | 1.68e-08 | 1.68e-08 | 1.4347e-08 | 1.8093e-09 | 1.7217e-07
Dioxin: 8D | 3268879 | 1.07e-07 | 1.07e-07 | 9.1378e-08 | 1.1524e-08 | 1.0965e-06
Formaldehyde | 50000 | 0.0705 | 0.0705 | 0.060207 | 0.0075928 | 0.72248
Furan: 4F Total | 55722275 | 3.34e-08 | 3.34e-08 | 2.8524e-08 | 3.5971e-09 | 3.4228e-07
Furan: 5F Total | 30402154 | 4.67e-08 | 4.67e-08 | 3.9882e-08 | 5.0295e-09 | 4.7858e-07
Furan: 6F Total | 55684941 | 2.41e-08 | 2.41e-08 | 2.0581e-08 | 2.5955e-09 | 2.4698e-07
Furan: 7F Total | 38998753 | 1.67e-08 | 1.67e-08 | 1.4262e-08 | 1.7986e-09 | 1.7114e-07
Furan: 8F | 39001020 | 8.61e-09 | 8.61e-09 | 7.3529e-09 | 9.2729e-10 | 8.8235e-08
HCL | 7647010 | 0.0809 | 0.0809 | 0.069089 | 0.0087128 | 0.82906
Indeno(1,2,3-cd)pyrene (PAH) | 193395 | 8.26e-05 | 8.26e-05 | 7.054e-05 | 8.8959e-06 | 0.00084648
Lead | 7439921 | 0.000608 | 0.000608 | 0.00051923 | 6.5481e-05 | 0.0062308
Manganese | 7439965 | 0.0103 | 0.0103 | 0.0087962 | 0.0011093 | 0.10555
Mercury | 7439976 | 2.71e-06 | 2.71e-06 | 2.3143e-06 | 2.9186e-07 | 2.7772e-05
Naphthalene (PAH) | 91203 | 0.0108 | 0.0108 | 0.0092232 | 0.0011631 | 0.11068
Nickel | 7440020 | 0.0488 | 0.0488 | 0.041675 | 0.0052557 | 0.5001
Selenium | 7782492 | 8.39e-06 | 8.39e-06 | 7.1651e-06 | 9.0359e-07 | 8.5981e-05
Zinc | 7440666 | 0.0538 | 0.0538 | 0.045945 | 0.0057942 | 0.55134
|  |  |  | 0.24743 |  | 2.9692
1. Annual based on twelve, one-hour test burns per year. 2. Controlled and Uncontrolled Air Toxics Emission Factor are identical.

## EF Criteria
DEVELOPMENT OF OIL READINESS TEST CRITERIA POLLUTANT
EMISSION FACTORS
FOR COMBUSTION TURBINES AT THE HARBOR PLANT
(Diesel Fuel Use by the Combustion Turbines)
1. The new combustion turbines (CTs) are GE LM6000 Sprint 47.3 MW (47,300 kW) turbine(1).
2. The heating input required is 8250 Btu/kW-hr (LHV), LM6000 GTG specifications(1).
3. The CTs will burn diesel oil for 30 minutes, 12 times for testing purposes. (2)
4. The SCR and CO Catalyst will not operate during the oil test. Water injection will begin after 5 minutes. (2)
5. The diesel fuel will have a HHV of 139,000 Btu/gal (3) and an estimated LHV of 126,000 Btu/gal.
6. Five minutes to achieve 7 mW and 30 minutes to full load. (2)
Calculate Maximum Firing Rate (MFR) for the CT in Btu/hr
Maximum Firing Rate = 47,300 kW X 8250 Btu/kW-hr
MFR | Size | Factor | LHV | HHV (3)
(Btu/hr) | (kW) | (Btu/kW-hr) | (Btu/gal) | (Btu/gal)
390225000 | 47300 | 8250 | 126000 | 139000
Maximum Hourly Fuel Consumption Rate (Mgal/hr) = MFR/(LHV x 1,000)
Maximum Hourly Fuel Consumption Rate (Mgal/hr) = |  |  |  | 3.097 | Mgal/hr
Fuel Consumption during test
Time | Fuel Use (2) | Fuel
(minutes) | (Btu) | (Mgal)
0 to 5 | 10500000 | 0.076
5 to 30 | 108150000 | 0.778
Convert Emission Factors from lbs/MMBtu to lbs/Mgal
EF (lbs/Mgal) = EF (lbs/MMBtu) x HHV (Btu/gal) /1000
ZERO TO FIVE MINUTES
| Pollutant | EF (3) | HHV | EF
|  | (lbs/MMBtu) | (Btu/gal) | (lbs/Mgal)
| NOx as NO2 | 0.637 | 139000 | 88.54
| CO | 0.0124 | 139000 | 1.72
| VOC as CH4 | 0.00803 | 139000 | 1.12
| PM10 | 0.012 | 139000 | 1.67
| SO2 | 0.051 | 139000 | 7.09
FIVE TO 30 MINUTES
| NOx as NO2 | 0.166 | 139000 | 23.07
| CO | 0.103 | 139000 | 14.32
| VOC as CH4 | 0.00803 | 139000 | 1.12
| PM10 | 0.012 | 139000 | 1.67
| SO2 | 0.051 | 139000 | 7.09
EL (lbs/MMBtu) = Exhaust Volume x Concentration x MW of Pollutant (5)
1,000,000 x 379
Exhaust Volume (DSCF/MMBtu) = 9190 DSCF/MMBtu x 20.9/(20.9 -%O2) (5)
Pollutant | Oxygen | Exhaust Vol | Conc. | MW | Fuel | EL
| (%) | (DSCF/MMBtu) | (ppmv) (6) | (lb/lb-mole) | (MMSCFH) | (lb/MMBtu)
NOx (NO2) | 15 | 32554.4068 | 42 | 46 | 0 | 0.166
Emission Factor for Sulfur Dioxide (SO2) (3)
| Pollutant | Emission | Sulfur | Emission
|  | Factor | Content | Factor
|  | (lbs/MMBtu) | (wt %) (4) | (lbs/MMBtu)
| SO2 | 1.01S | 0.05 | 0.051
(1) Specification provided by LA DWP from Request for Proposal dated September 25, 2000 and
S & S Energy Products' Specifications sheet.
(2) Information provided by LA DWP in an e-mail to Krishna Nand on 10/26/00.
(3) Taken from AP-42, Section 3.1. Emission factors are all load emission factors
AP-42 Combustion Turbine Emission Factor Documentation, Table 3.4-2.
Sulfur Dioxide and PM emission factor is from AP-42, Table 3.1-2a.
Emission Factors from Emission Factor Documentation is inconsistent.
(4) Maximum value for #2 diesel oil.
(5) Taken from SCAQMD Title V Technical Guidance Manual, page A-20, 1998.
EPA Method 19, 40 CFR Part 60
(6) Guaranteed emission from GE.

## Stack Calc
DEVELOPMENT OF THE STACK GAS FLOW RATE
FOR THE COMBUSTION TURBINES AT THE HARBOR PLANT
(No. 2 Diesel Fuel Use by the Combustion Turbines)
1. The new combustion turbines (CTs) are GE LM6000 Sprints 47.3 MW (47,300 kW) turbine(1).
2. The heating input required is 8250 Btu/kW-hr (LHV), LM6000 GTG specifications(1).
3. The CTs will burn diesel oil for one hour, twelve times each year for testing purposes. (3)
4. The SCR will not be operational during the oil firing period. (3)
5. The diesel fuel will have a HHV of 139,000 Btu/gal (2) and an estimated LHV of 126,000 Btu/gal.
6. The assumed stack gas O2 content is 15%.
Calculate Maximum Firing Rate (MFR) for the CT in Btu/hr
Maximum Firing Rate = 47,300 kW X 8250 Btu/kW-hr
MFR | Size | Factor | LHV | HHV
(Btu/hr) | (kW) | (Btu/kW-hr) | (Btu/gal) | (Btu/gal)
390225000 | 47300 | 8250 | 126000 | 139000
Maximum Hourly Fuel Consumption Rate (Mgal) = MFR/(LHV x 1,000)
Total Fuel Burned During Readiness Test from DWP (2) = |  |  |  | 0.854 | Mgal/30min
Fuel Burned During First Five Minutes |  |  | 0.076 | Mgal
Exhaust Volume (WSCF/MMBtu) = 10,320 WSCF/MMBtu x 20.9/(20.9 -%O2) (3)(4)
Stack Gas Flow Rate, ACF = |  | Stack Gas Flow (SCF) x |  | [Stack Gas Temp (oR)]
[Standard Temp (oR)]
oR = oF + 460
Standard Temp = 60 oF
Unit | Oxygen | Exhaust Vol | Heat Input | Exhaust Flow | Stack Temp. | Exhaust Flow | Exhaust Flow
| (%) | (WSCF/MMBtu) | (MMBtu/time) | (WSCF) | (oF) | (WACF) | (WACFS)
CT #1-5, 0 to 5min | 15 | 36557.2881 | 10.5 | 383852 | 100 | 413379 | 1378
CT #1-5, 0 to 30min | 15 | 36557.2881 | 118.7 | 4339350 | 117 | 4815010 | 2675
Unit | Stack Inside Diameter(2) | Stack Exit Velocity | Stack Exit Velocity | Stack Inside Diameter | Stack Height(2) | Stack Height
| (FT) | (FT/SEC) | (M/SEC) | (M) | (FT) | (M)
CT #1-5, 0 to 5min | 10 | 17.55 | 5.35 | 3.05 | 110 | 33.53
CT #1-5, 0 to 30min | 10 | 34.06 | 10.38 | 3.05 | 110 | 33.53
(1) Specification provided by LA DWP from Request for Proposal dated September 25, 2000 and
and S & S Energy Products' Specifications sheet.
(2) SCR Bid specification (no. 9628) from LA DWP and information in a e-mails to Krishna Nand
received on 10/18/00 and 11/01/00.
(3) Taken from SCAQMD Title V Technical Guidance Manual, page A-20, 1998. Used oil F factor, wet.
(4) EPA Method 19, 40 CFR Part 60.

## Air Toxics EF
CARB AIR TOXICS EMISSION FACTORS
COMBUSTION TURBINES -- Diesel Fuel
Air Toxics Emission factors are from California Air Resources Board's latest air toxics data
base. These emission factors are for combustion turbines equipped with SCR and CO
catalysts. The data were provided by CARB on 10/12/00 (fax from Kirk Rosenkranz to Krishna
Nand Tel. No. 916/322-7673).
Substance | Air Toxic | CAS No. | Rule 1401 | Mean Emission
Category |  |  | Listed Air | Factor
|  |  | Toxic (Y/N) | (lbs/MGAL)
PAH | Acenaphthene (PAH) | 83329 | N | 9.69e-05
PAH | Acenaphthylene (PAH) | 208968 | N | 8.61e-05
PAH | Anthracene (PAH) | 120127 | N | 9.8e-05
Metal | Arsenic | 7440382 | Y | 0.000202
PAH | Benz(a)anthracene (PAH) | 56553 | Y | 8.53e-05
VOC | Benzene | 71432 | Y | 0.0113
PAH | Benzo(a)pyrene (PAH) | 50328 | Y | 8.33e-05
PAH | Benzo(b)fluoranthene (PAH) | 205992 | Y | 0.000132
PAH | Benzo(b+k)fluoranthene (PAH) | --- | N | 3.23e-06
PAH | Benzo(g,h,i)perylene (PAH) | 191242 | N | 8.26e-05
PAH | Benzo(k)fluoranthene (PAH) | 207089 | Y | 0.00013
Metal | Beryllium | 7440417 | Y | 5.43e-05
Metal | Cadmium | 7440439 | Y | 0.000325
PAH | Chrysene (PAH) | 218019 | Y | 0.000103
Metal | Chromium (Hex) | 18540299 | Y | 1.08e-05
Metal | Chromium (total) | 7440473 | Y | 0.000424
Metal | Copper | 7440508 | Y | 0.000998
PAH | Dibenz(a,h)anthracene (PAH) | 53703 | Y | 8.25e-05
Diox/Furan | Dioxin: 4D Total | 41903575 | Y | 3.74e-09
Diox/Furan | Dioxin: 5D Total | 36088229 | Y | 7.15e-09
Diox/Furan | Dioxin: 6D Total | 34465468 | Y | 9e-09
Diox/Furan | Dioxin: 7D Total | 37871004 | Y | 1.68e-08
Diox/Furan | Dioxin: 8D | 3268879 | Y | 1.07e-07
PAH | Fluoranthene (PAH) | 206440 | N | 0.000125
PAH | Fluorene (PAH) | 86737 | N | 0.000127
VOC | Formaldehyde | 50000 | Y | 0.0705
Diox/Furan | Furan: 4F Total | 55722275 | Y | 3.34e-08
Diox/Furan | Furan: 5F Total | 30402154 | Y | 4.67e-08
Diox/Furan | Furan: 6F Total | 55684941 | Y | 2.41e-08
Diox/Furan | Furan: 7F Total | 38998753 | Y | 1.67e-08
Diox/Furan | Furan: 8F | 39001020 | Y | 8.61e-09
Halogens | HCL | 7647010 | Y | 0.0809
PAH | Indeno(1,2,3-cd)pyrene (PAH) | 193395 | Y | 8.26e-05
Metals | Lead | 7439921 | Y | 0.000608
Metals | Managanese | 7439965 | Y | 0.0103
Metals | Mercury | 7439976 | Y | 2.71e-06
PAH | Naphthalene (PAH) | 91203 | Y | 0.0108
Metals | Nickel | 7440020 | Y | 0.0488
PAH | Phenanthrene PAH) | 85018 | N | 0.000412
PAH | Pyrene (PAH) | 129000 | N | 0.000101
Metals | Selenium | 7782492 | Y | 8.39e-06
Metals | Zinc | 7440666 | Y | 0.0538