## stack
Development of Stack Parameters
At the Scattergood Plant
1. The Scattergood Plant has three boilers that will be fitted with SCR. Boilers No. 1 and No. 2
have a maximum natural gas consumption of 1685 mscfh each and Boiler No. 3 has a maximum
natural gas consumption rate of 4140 mscfh. (1)
2. The stack gas flow rate for Boiler No.1 and Boiler No. 2 is 1,595,000 lbs/hr. The temperature
is 294 oF. Boilers Nos.1 and 2 exhaust through a common stack, Stack No. 1. (1)
3. The stack gas flow rate for Boiler No. 3 is 3,641,000 lbs/hr. The temperature is 271 oF. (1)
4. Boiler No. 3 exhaust through a separate stack, Stack No. 2. (1)
5. Standard temperature is assumed to be 60 oF.
6. The assumed stack gas O2 content is 3%.
7. The assumed stack gas molecular weight is 28.
Calculate the Stack Gas Flow Rate
Stack Gas Flow Rate, SCFH = |  | Stack Gas Flow (lbs/hr) x 379 (scf/lb-mole)
MW (lbs/lb-mole)
Stack Gas Flow Rate, ACFH = |  | Stack Gas Flow (SCFH) x |  | [Stack Gas Temp (oR)]
[Standard Temp (oR)]
Unit 1 Exhaust Flow = |  | 1595000 | lbs/hr | Unit 2 Exhaust Flow = |  | 1595000 | lbs/hr
Unit 3 Exhaust Flow = |  | 3641000 | lbs/hr
Stack No. | Stack Gas Flow | Stack Gas MW | Stack Gas Temp | Stack Gas Flow | Stack Gas Flow | Stack Gas Flow | Stack Gas Flow
| (lbs/hr) | (lb/lb-mole) | (oF) | (SCFH) | (ACFH) | (SCFM) | (ACFM)
Number 1 | 3190000 | 28 | 294 | 43178929 | 62609447 | 719649 | 1043491
Number 2 | 3641000 | 28 | 271 | 49283536 | 69281278 | 821392 | 1154688
Stack No. | Stack Inside Diameter(2) | Stack Exit Velocity | Stack Exit Velocity | Stack Inside Diameter | Stack Height(2) | Stack Height
| (FT) | (FT/SEC) | (M/SEC) | (M) | (FT) | (M)
Number 1 | 20 | 55.36 | 16.87 | 6.1 | 300 | 91.44
Number 2 | 23.5 | 44.37 | 13.52 | 7.16 | 330 | 100.58
(1) Information provided by LA DWP.
(2) Information from LA DWP in e-mail from Tim Conkin dated 10/18/00.