## Criteria Pollu. Emissions
DWP VALLEY STATION -- CRITERIA POLLUTANT EMISSIONS
COMMISSIONING SCENARIO
No. 2 Diesel Fuel Use by the Combustion Turbine
Device ID Number: | Combustion Turbine #1
Process Description:
No. of Devices: | 1
Process Equipment Description: | GE LM6000, Sprint 47.3 MW
Fuel Type: | No. 2 Diesel Fuel
Process Units: | Mgal
Control Equipment: | Selective Catalytic Reduction, CO Catalyst, and
water-steam injection for controlled operation.
Yearly Emis. Est. Equation: | Fy x EF
Max Hourly Emis. Est. Equation: | Fm x EF
Parameter Symbols/Names |  |  | Values
Fy = Total Yearly Amount of Fuel Burned (one CT) |  |  | NA | Mgal
F1 = Average Fuel with no control during hour 0 to 5. |  |  | 0.906 | Mgal/hr
F2 = Fuel with water injection hour 6 to 10. |  |  | 1.919 | Mgal/hr
EF = Emission Factor |  |  | See below | lbs/Mgal
Process Operation Schedule | 5 | hours at no control
| 5 | hours with water inection
| Hour 0 to 5 | Hour 6 to 10 | Remainder | Hour 0 to 5 | Hour 6 to 10
Criteria | Emission | Emission | Emission
Species Name | Factor | Factor | Factor | Emissions | Emissions
| (lb/Mgal) | (lb/Mgal) | (lbs/Mgal) | (lbs/hr) | (lbs/hr)
NOx | 88.54 | 23.07 | 2.75 | 80.2172 | 44.2713
CO | 1.72 | 14.32 | 2 | 1.5583 | 27.4801
VOC | 1.12 | 1.12 | 0.38 | 1.0147 | 2.1493
PM10 | 1.67 | 1.67 | 1.67 | 1.513 | 3.2047
SO2 | 7.09 | 7.09 | 7.09 | 6.4235 | 13.6057
| Total | Hour 0 to 5 | Hour 6 to 10 | Total
Criteria | Commissioning | Hourly | Hourly | Commissioning
Species Name | Emissions | Emissions | Emissions | Hrly Emissions
| (lbs) | (grams/sec) | (grams/sec) | (grams/sec)
NOx | 622.4429 | 10.12 | 5.5831 | 7.8497
CO | 145.192 | 0.2 | 3.4655 | 1.831
VOC | 15.82 | 0.13 | 0.27105 | 0.19951
PM10 | 23.5888 | 0.19 | 0.40415 | 0.29748
SO2 | 100.1462 | 0.81 | 1.7158 | 1.263

## Toxic Emissions
DWP VALLEY STATION --AIR TOXIC POLLUTANT EMISSIONS
COMMISSIONING SCENARIO
No. 2 Diesel Fuel Use by the Combustion Turbine
Device ID Number: | Combustion Turbine #1
Process Description:
No. of Devices: | 1
Process Equipment Description: | GE LM6000, Sprint 47.3 MW
Fuel Type: | No. 2 Diesel Fuel
Process Units: | Mgal
Control Equipment: | Selective Catalytic Reduction, CO Catalyst, and
water-steam injection for controlled operation.
Yearly Emis. Est. Equation: | Fy x EF
Max Hourly Emis. Est. Equation: | Fm x EF
Parameter Symbols/Names |  |  | Values
Fy = Total Yearly Amount of Fuel Burned (one CT) |  |  | NA | Mgal
F1 = Average Fuel with no control during hour 0 to 5. |  |  | 0.906 | Mgal/hr
F2 = Fuel with water injection hour 6 to 10. |  |  | 1.919 | Mgal/hr
EF = Emission Factor |  |  | See below | lbs/Mgal
Process Operation Schedule | 5 | hours at no control
| 5 | hours with water inection
| Emittent ID | Hour 0 to 10 | Hour 0 to 5 | Hour 6 to 10 | Total
Criteria | (CAS Number) | Emission |  |  | Commissioning
Species Name |  | Factor (1) | Emissions | Emissions | Emissions
|  | (lb/Mgal) | (lbs/hr) | (lbs/hr) | (lbs)
Arsenic | 7440382 | 0.000202 | 0.00018301 | 0.00038764 | 0.0028532
Benz(a)anthracene (PAH) | 56553 | 8.53e-05 | 7.7282e-05 | 0.00016369 | 0.0012049
Benzene | 71432 | 0.0113 | 0.010238 | 0.021685 | 0.15961
Benzo(a)pyrene (PAH) | 50328 | 8.33e-05 | 7.547e-05 | 0.00015985 | 0.0011766
Benzo(b)fluoranthene (PAH) | 205992 | 0.000132 | 0.00011959 | 0.00025331 | 0.0018645
Benzo(k)fluoranthene (PAH) | 207089 | 0.00013 | 0.00011778 | 0.00024947 | 0.0018362
Beryllium | 7440417 | 5.43e-05 | 4.9196e-05 | 0.0001042 | 0.00076699
Cadmium | 7440439 | 0.000325 | 0.00029445 | 0.00062367 | 0.0045906
Chrysene (PAH) | 218019 | 0.000103 | 9.3318e-05 | 0.00019766 | 0.0014549
Chromium (Hex) | 18540299 | 1.08e-05 | 9.7848e-06 | 2.0725e-05 | 0.00015255
Chromium (total) | 7440473 | 0.000424 | 0.00038414 | 0.00081366 | 0.005989
Copper | 7440508 | 0.000998 | 0.00090419 | 0.0019152 | 0.014097
Dibenz(a,h)anthracene (PAH) | 53703 | 8.25e-05 | 7.4745e-05 | 0.00015832 | 0.0011653
Dioxin: 4D Total | 41903575 | 3.74e-09 | 3.3884e-09 | 7.1771e-09 | 5.2827e-08
Dioxin: 5D Total | 36088229 | 7.15e-09 | 6.4779e-09 | 1.3721e-08 | 1.0099e-07
Dioxin: 6D Total | 34465468 | 9e-09 | 8.154e-09 | 1.7271e-08 | 1.2712e-07
Dioxin: 7D Total | 37871004 | 1.68e-08 | 1.5221e-08 | 3.2239e-08 | 2.373e-07
Dioxin: 8D | 3268879 | 1.07e-07 | 9.6942e-08 | 2.0533e-07 | 1.5114e-06
Formaldehyde | 50000 | 0.0705 | 0.063873 | 0.13529 | 0.99581
Furan: 4F Total | 55722275 | 3.34e-08 | 3.026e-08 | 6.4095e-08 | 4.7178e-07
Furan: 5F Total | 30402154 | 4.67e-08 | 4.231e-08 | 8.9617e-08 | 6.5964e-07
Furan: 6F Total | 55684941 | 2.41e-08 | 2.1835e-08 | 4.6248e-08 | 3.4041e-07
Furan: 7F Total | 38998753 | 1.67e-08 | 1.513e-08 | 3.2047e-08 | 2.3589e-07
Furan: 8F | 39001020 | 8.61e-09 | 7.8007e-09 | 1.6523e-08 | 1.2162e-07
HCL | 7647010 | 0.0809 | 0.073295 | 0.15525 | 1.1427
Indeno(1,2,3-cd)pyrene (PAH) | 193395 | 8.26e-05 | 7.4836e-05 | 0.00015851 | 0.0011667
Lead | 7439921 | 0.000608 | 0.00055085 | 0.0011668 | 0.008588
Manganese | 7439965 | 0.0103 | 0.0093318 | 0.019766 | 0.14549
Mercury | 7439976 | 2.71e-06 | 2.4553e-06 | 5.2005e-06 | 3.8279e-05
Naphthalene (PAH) | 91203 | 0.0108 | 0.0097848 | 0.020725 | 0.15255
Nickel | 7440020 | 0.0488 | 0.044213 | 0.093647 | 0.6893
Selenium | 7782492 | 8.39e-06 | 7.6013e-06 | 1.61e-05 | 0.00011851
Zinc | 7440666 | 0.0538 | 0.048743 | 0.10324 | 0.75992
| Emittent ID |  | Hour 0 to 5 | Hour 6 to 10 | Total
Criteria | (CAS Number) |  | Hourly | Hourly | Commissioning
Species Name |  |  | Emissions | Emissions | Hrly Emissions
|  |  | (grams/sec) | (grams/sec) | (grams/sec)
Arsenic | 7440382 |  | 2.308e-05 | 4.8885e-05 | 3.5983e-05
Benz(a)anthracene (PAH) | 56553 |  | 9.7461e-06 | 2.0643e-05 | 1.5195e-05
Benzene | 71432 |  | 0.0012911 | 0.0027347 | 0.0020129
Benzo(a)pyrene (PAH) | 50328 |  | 9.5176e-06 | 2.0159e-05 | 1.4838e-05
Benzo(b)fluoranthene (PAH) | 205992 |  | 1.5082e-05 | 3.1945e-05 | 2.3513e-05
Benzo(k)fluoranthene (PAH) | 207089 |  | 1.4853e-05 | 3.1461e-05 | 2.3157e-05
Beryllium | 7440417 |  | 6.2041e-06 | 1.3141e-05 | 9.6726e-06
Cadmium | 7440439 |  | 3.7133e-05 | 7.8652e-05 | 5.7893e-05
Chrysene (PAH) | 218019 |  | 1.1768e-05 | 2.4927e-05 | 1.8348e-05
Chromium (Hex) | 18540299 |  | 1.234e-06 | 2.6137e-06 | 1.9238e-06
Chromium (total) | 7440473 |  | 4.8445e-05 | 0.00010261 | 7.5528e-05
Copper | 7440508 |  | 0.00011403 | 0.00024152 | 0.00017778
Dibenz(a,h)anthracene (PAH) | 53703 |  | 9.4262e-06 | 1.9966e-05 | 1.4696e-05
Dioxin: 4D Total | 41903575 |  | 4.2732e-10 | 9.0511e-10 | 6.6621e-10
Dioxin: 5D Total | 36088229 |  | 8.1694e-10 | 1.7304e-09 | 1.2736e-09
Dioxin: 6D Total | 34465468 |  | 1.0283e-09 | 2.1781e-09 | 1.6032e-09
Dioxin: 7D Total | 37871004 |  | 1.9195e-09 | 4.0657e-09 | 2.9926e-09
Dioxin: 8D | 3268879 |  | 1.2225e-08 | 2.5895e-08 | 1.906e-08
Formaldehyde | 50000 |  | 0.0080551 | 0.017062 | 0.012558
Furan: 4F Total | 55722275 |  | 3.8162e-09 | 8.083e-09 | 5.9496e-09
Furan: 5F Total | 30402154 |  | 5.3358e-09 | 1.1302e-08 | 8.3188e-09
Furan: 6F Total | 55684941 |  | 2.7536e-09 | 5.8324e-09 | 4.293e-09
Furan: 7F Total | 38998753 |  | 1.9081e-09 | 4.0415e-09 | 2.9748e-09
Furan: 8F | 39001020 |  | 9.8375e-10 | 2.0837e-09 | 1.5337e-09
HCL | 7647010 |  | 0.0092434 | 0.019578 | 0.014411
Indeno(1,2,3-cd)pyrene (PAH) | 193395 |  | 9.4376e-06 | 1.999e-05 | 1.4714e-05
Lead | 7439921 |  | 6.9468e-05 | 0.00014714 | 0.0001083
Manganese | 7439965 |  | 0.0011768 | 0.0024927 | 0.0018348
Mercury | 7439976 |  | 3.0964e-07 | 6.5584e-07 | 4.8274e-07
Naphthalene (PAH) | 91203 |  | 0.001234 | 0.0026137 | 0.0019238
Nickel | 7440020 |  | 0.0055757 | 0.01181 | 0.0086928
Selenium | 7782492 |  | 9.5861e-07 | 2.0304e-06 | 1.4945e-06
Zinc | 7440666 |  | 0.006147 | 0.01302 | 0.0095835
1. Controlled and Uncontrolled Air Toxics Emission Factor are identical.

## EF Criteria
DEVELOPMENT OF COMMISSIONING EMISSION FACTORS
EMISSION FACTORS
FOR COMBUSTION TURBINE AT THE VALLEY PLANT
(No. 2 Diesel Fuel Use by the Combustion Turbine)
1. The new combustion turbine (CT) is a GE LM6000 Sprint 47.3 MW (47,300 kW) turbine(1).
2. The heating input required is 8250 Btu/kW-hr (LHV), LM6000 GTG specifications(1).
3. The CT will take 10 hours to reach full power. (2)
4. Water injection will begin after five hours. SCR and CO catylst operation will not operate.(2)
5. The CT will use No. 2 Diesel Fuel with a HHV of 139,000 Btu/gal (2).
6. Controlled emission limits are 5 ppmv for oxides of nitrogen (NOx), 6 ppmv for carbon monoxide (CO),
2 ppmv for volatile organic compounds (VOC), and 5 ppmv for ammonia (NH3)(3) for controlled operations.
7. Emission limits are assumed to be at 15% O2.
Calculate Maximum Firing Rate (MFR) for the CT in Btu/hr
Maximum Firing Rate = 47,300 kW X 8250 Btu/kW-hr
MFR | Size | Factor | LHV | HHV
(Btu/hr) | (kW) | (Btu/kW-hr) | (Btu/gal) | (Btu/gal)
390225000 | 47300 | 8250 | 126000 | 139000
Maximum Hourly Fuel Consumption Rate (Mgal) = MFR/(LHV x 1,000)
Maximum Hourly Fuel Consumption Rate (Mgal/hr) = |  |  |  | 3.097 | Mgal/hr
Fuel Consumption during test
Time | Heat Input (2) | Fuel
(hours) | (Btu/hr) | (Mgal/hr)
0 to 5 | 126000000 | 0.906
6 to 10 | 266700000 | 1.919
Convert Emission Factors from lbs/MMBtu to lbs/MMscf
EF (lbs/Mgal) = EF (lbs/MMBtu) x HHV (Btu/gal) / 1,000
ZERO TO FIVE HOURS
| Pollutant | EF (5) | HHV | EF
|  | (lbs/MMBtu) | (Btu/gal) | (lbs/Mgal)
| NOx as NO2 | 0.637 | 139000 | 88.54
| CO | 0.0124 | 139000 | 1.72
| VOC as CH4 | 0.00803 | 139000 | 1.12
SIX TO TEN HOURS
| Pollutant | EF (5) | HHV | EF
|  | (lbs/MMBtu) | (Btu/gal) | (lbs/Mgal)
| NOx as NO2 | 0.166 | 139000 | 23.07
| CO | 0.103 | 139000 | 14.32
| VOC as CH4 | 0.00803 | 139000 | 1.12
Convert Emission Limits (EL) from ppmv to lb/MMBtu for NOx, CO, VOC, and NH3 (controlled operations).
EL (lbs/MMBtu) = Exhaust Volume x Concentration x MW of Pollutant (6)
1,000,000 x 379
Exhaust Volume (DSCF/MMBtu) = 9190 DSCF/MMBtu x 20.9/(20.9 -%O2) (7)
Pollutant | Oxygen | Exhaust Vol | Conc. | MW |  | EL
| (%) | (DSCF/MMBtu) | (ppmv) | (lb/lb-mole) |  | (lb/MMBtu)
NOx (NO2) | 15 | 32554.4068 | 42 | 46 |  | 0.166
NOx (NO2) | 15 | 32554.4068 | 5 | 46 |  | 0.0198
CO | 15 | 32554.4068 | 6 | 28 |  | 0.0144
VOC (CH4) | 15 | 32554.4068 | 2 | 16 |  | 0.0027
NH3 | 15 | 32554.4068 | 5 | 17 |  | 0.0073
Convert Emission Limit (EL) in lb/MMBtu to Emission Factor in lb/MMscf, EF = EL x HHV (Btu/scf)
| Pollutant | EL | HHV | EF
|  | (lb/MMBtu) | (Btu/gal) | (lb/Mgal)
| NOx (NO2) | 0.0198 | 139000 | 2.75
| CO | 0.0144 | 139000 | 2
| VOC (CH4) | 0.0027 | 139000 | 0.38
| NH3 | 0.0073 | 139000 | 1.01
Emission Factors for PM10 and Sulfur Dioxide (SO2) all times
| Pollutant | Emission | HHV | Emission
|  | Factor | (Btu/gal) | Factor
|  | (lb/MMBtu) |  | (lb/Mgal)
| PM10 (5) | 0.012 | 139000 | 1.67
| SO2 (5) | 0.051 | 139000 | 7.09
Emission Factor for Sulfur Dioxide (SO2) (4)
| Pollutant | Emission | Sulfur | Emission
|  | Factor | Content | Factor
|  | (lbs/MMBtu) | (wt %) (5) | (lbs/MMBtu)
| SO2 | 1.01S | 0.05 | 0.051
Exhaust Volume (WSCF/MMBtu) = 10,320 WSCF/MMBtu x 20.9/(20.9 -%O2)
Stack Gas Flow Rate, ACFH = |  | Stack Gas Flow (SCFH) x |  | [Stack Gas Temp (oR)]
[Standard Temp (oR)]
oR = oF + 460
Standard Temp = 60 oF
Unit | Oxygen | Exhaust Vol | Max Firing | Exhaust Flow | Stack Temp. | Exhaust Flow | Exhaust Flow
| (%) | (WSCF/MMBtu) | (MMBtu/hr) | (WSCFH) | (oF) | (WACFH) | (WACFS)
CT#1 0 to 5 hours | 15 | 36557.2881 | 126 | 4606218 | 824 | 11373815 | 3159
CT#1 6 to 10 hours | 15 | 36557.2881 | 266.7 | 9749829 | 824 | 24074578 | 6687
Unit | Stack Inside Diameter(9) | Stack Exit Velocity | Stack Exit Velocity | Stack Inside Diameter | Stack Height(9) | Stack Height
| (FT) | (FT/SEC) | (M/SEC) | (M) | (FT) | (M)
CT#1 0 to 5 hours | 10 | 40.22 | 12.26 | 3.05 | 110 | 33.53
CT#1 6 to 10 hours | 10 | 85.14 | 25.95 | 3.05 | 110 | 33.53
(1) Specification provided by LA DWP from Request for Proposal dated September 25, 2000 and
S & S Energy Products' Specifications sheet.
(2) Information provided by LA DWP in an e-mail to Krishna Nand on 11/01/00.
(3) Specifications from LA DWP (Generation - 2000 Project Overview)
(4) SCR Bid specification (no. 9628) from LA DWP.
(5) Taken from AP-42, Section 3.1. Emission factors are all load emission factors
AP-42 Combustion Turbine Emission Factor Development Document, Table 3.4-1.
PM10 and Sulfur Dioxide emission factor is from AP-42, Table 3.1-2a. NOx factor is GE guarantee.
(6) Taken from SCAQMD Title V Technical Guidance Manual, page A-20, 1998.
(7) EPA Method 19, 40 CFR Part 60.
(8) Emission Factor in lb/MMBtu is from AP-42, Table 3.1-1 and Table 3.1-2a.
(9) Information provided by DWP in an e-mail to Krishna Nand on 10/18/00.

## Air Toxics EF
CARB AIR TOXICS EMISSION FACTORS
COMBUSTION TURBINES -- Diesel Fuel
Air Toxics Emission factors are from California Air Resources Board's latest air toxics data
base. These emission factors are for combustion turbines equipped with SCR and CO
catalysts. The data were provided by CARB on 10/12/00 (fax from Kirk Rosenkranz to Krishna
Nand Tel. No. 916/322-7673).
Substance | Air Toxic | CAS No. | Rule 1401 | Mean Emission
Category |  |  | Listed Air | Factor
|  |  | Toxic (Y/N) | (lbs/MGAL)
PAH | Acenaphthene (PAH) | 83329 | N | 9.69e-05
PAH | Acenaphthylene (PAH) | 208968 | N | 8.61e-05
PAH | Anthracene (PAH) | 120127 | N | 9.8e-05
Metal | Arsenic | 7440382 | Y | 0.000202
PAH | Benz(a)anthracene (PAH) | 56553 | Y | 8.53e-05
VOC | Benzene | 71432 | Y | 0.0113
PAH | Benzo(a)pyrene (PAH) | 50328 | Y | 8.33e-05
PAH | Benzo(b)fluoranthene (PAH) | 205992 | Y | 0.000132
PAH | Benzo(b+k)fluoranthene (PAH) | --- | N | 3.23e-06
PAH | Benzo(g,h,i)perylene (PAH) | 191242 | N | 8.26e-05
PAH | Benzo(k)fluoranthene (PAH) | 207089 | Y | 0.00013
Metal | Beryllium | 7440417 | Y | 5.43e-05
Metal | Cadmium | 7440439 | Y | 0.000325
PAH | Chrysene (PAH) | 218019 | Y | 0.000103
Metal | Chromium (Hex) | 18540299 | Y | 1.08e-05
Metal | Chromium (total) | 7440473 | Y | 0.000424
Metal | Copper | 7440508 | Y | 0.000998
PAH | Dibenz(a,h)anthracene (PAH) | 53703 | Y | 8.25e-05
Diox/Furan | Dioxin: 4D Total | 41903575 | Y | 3.74e-09
Diox/Furan | Dioxin: 5D Total | 36088229 | Y | 7.15e-09
Diox/Furan | Dioxin: 6D Total | 34465468 | Y | 9e-09
Diox/Furan | Dioxin: 7D Total | 37871004 | Y | 1.68e-08
Diox/Furan | Dioxin: 8D | 3268879 | Y | 1.07e-07
PAH | Fluoranthene (PAH) | 206440 | N | 0.000125
PAH | Fluorene (PAH) | 86737 | N | 0.000127
VOC | Formaldehyde | 50000 | Y | 0.0705
Diox/Furan | Furan: 4F Total | 55722275 | Y | 3.34e-08
Diox/Furan | Furan: 5F Total | 30402154 | Y | 4.67e-08
Diox/Furan | Furan: 6F Total | 55684941 | Y | 2.41e-08
Diox/Furan | Furan: 7F Total | 38998753 | Y | 1.67e-08
Diox/Furan | Furan: 8F | 39001020 | Y | 8.61e-09
Halogens | HCL | 7647010 | Y | 0.0809
PAH | Indeno(1,2,3-cd)pyrene (PAH) | 193395 | Y | 8.26e-05
Metals | Lead | 7439921 | Y | 0.000608
Metals | Managanese | 7439965 | Y | 0.0103
Metals | Mercury | 7439976 | Y | 2.71e-06
PAH | Naphthalene (PAH) | 91203 | Y | 0.0108
Metals | Nickel | 7440020 | Y | 0.0488
PAH | Phenanthrene PAH) | 85018 | N | 0.000412
PAH | Pyrene (PAH) | 129000 | N | 0.000101
Metals | Selenium | 7782492 | Y | 8.39e-06
Metals | Zinc | 7440666 | Y | 0.0538